## Copyright-Notices
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
This machine discharge energy calculator is part of IEEE Std 1349-2021, Guide for the Application of Electric Machines in Zone 2 and Class I, Division 2 Hazardous (Classified) Locations.
Copyright © 2021 by The Institute of Electrical and Electronics Engineers, Inc. Three Park Avenue New York, New York 10016-5997, USA All rights reserved.
IEEE is a registered trademark in the U.S. Patent & Trademark Office, owned by The Institute of Electrical and Electronics Engineers, Incorporated. IEEE prohibits discrimination, harassment, and bullying. For more information, visit https:// www .ieee .org/ web/ aboutus/ whatis/ policies/ p9 -26 .html.
Copyrights
IEEE draft and approved standards are copyrighted by IEEE under US and international copyright laws. They are made available by IEEE and are adopted for a wide variety of both public and private uses. These include both use, by reference, in laws and regulations, and use in private self-regulation, standardization, and the promotion of engineering practices and methods. By making these documents available for use and adoption by public authorities and private users, IEEE does not waive any rights in copyright to the documents.
Every effort has been made to secure permission to reprint borrowed material contained in this document. If omissions have been made, please bring them to our attention.
Important Notices and Disclaimers Concerning IEEE Standards Documents
IEEE Standards documents are made available for use subject to important notices and legal disclaimers. These notices and disclaimers, or a reference to this page (https://standards.ieee.org/ipr/disclaimers.html), appear in all standards and may be found under the heading “Important Notices and Disclaimers Concerning IEEE Standards Documents.”
Notice and Disclaimer of Liability Concerning the Use of IEEE Standards Documents
IEEE Standards documents are developed within the IEEE Societies and the Standards Coordinating Committees of the IEEE Standards Association (IEEE SA) Standards Board. IEEE develops its standards through an accredited consensus development process, which brings together volunteers representing varied viewpoints and interests to achieve the final product. IEEE Standards are documents developed by volunteers with scientific, academic, and industry-based expertise in technical working groups. Volunteers are not necessarily members of IEEE or IEEE SA, and participate without compensation from IEEE. While IEEE administers the process and establishes rules to promote fairness in the consensus development process, IEEE does not independently evaluate, test, or verify the accuracy of any of the information or the soundness of any judgments contained in its standards.
IEEE makes no warranties or representations concerning its standards, and expressly disclaims all warranties, express or implied, concerning this standard, including but not limited to the warranties of merchantability, fitness for a particular purpose and non-infringement. In addition, IEEE does not warrant or represent that the use of the material contained in its standards is free from patent infringement. IEEE standards documents are supplied “AS IS” and “WITH ALL FAULTS.”
Use of an IEEE standard is wholly voluntary. The existence of an IEEE Standard does not imply that there are no other ways to produce, test, measure, purchase, market, or provide other goods and services related to the scope of the IEEE standard. Furthermore, the viewpoint expressed at the time a standard is approved and issued is subject to change brought about through developments in the state of the art and comments received from users of the standard.
In publishing and making its standards available, IEEE is not suggesting or rendering professional or other services for, or on behalf of, any person or entity, nor is IEEE undertaking to perform any duty owed by any other person or entity to another. Any person utilizing any IEEE Standards document, should rely upon his or her own independent judgment in the exercise of reasonable care in any given circumstances or, as appropriate, seek the advice of a competent professional in determining the appropriateness of a given IEEE standard.
IN NO EVENT SHALL IEEE BE LIABLE FOR ANY DIRECT, INDIRECT, INCIDENTAL, SPECIAL, EXEMPLARY, OR CONSEQUENTIAL DAMAGES (INCLUDING, BUT NOT LIMITED TO: THE NEED TO PROCURE SUBSTITUTE GOODS OR SERVICES; LOSS OF USE, DATA, OR PROFITS; OR BUSINESS INTERRUPTION) HOWEVER CAUSED AND ON ANY THEORY OF LIABILITY, WHETHER IN CONTRACT, STRICT LIABILITY, OR TORT (INCLUDING NEGLIGENCE OR OTHERWISE) ARISING IN ANY WAY OUT OF THE PUBLICATION, USE OF, OR RELIANCE UPON ANY STANDARD, EVEN IF ADVISED OF THE POSSIBILITY OF SUCH DAMAGE AND REGARDLESS OF WHETHER SUCH DAMAGE WAS FORESEEABLE.
IEEE Standards Department 445 Hoes Lane Piscataway, NJ 08854, USA

## Salient Pole Synch. Machine
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
CAPACITANCE AND ENERGY CALCULATIONS |  |  |  |  | Metric Units
[5 empty] | Version 2021.0 | 2021-06-16
SALIENT POLE MACHINE |  |  |  |  | REF:
MACHINE CAPACITANCES
Blue Highlighted cells are explanatory
Yellow Highlighted cells require data entry |  | OD = Outer diameter
Purple Highlighted cells are calculated answers |  | ID = Inner diameter
Stator and Rotor Data
Stator Length | L1 | 1.17 | m
Rotor Length | L2 (= L1 typically) | 1.17 | m
Rotor Diameter (OD) | D1 | 1.35 | m
Stator to Rotor Main Air Gap | DAG | 0.03 | m
Þ Stator diameter (ID) | D2 = D1 + 2DAG | 1.41 | m
Stator to Rotor Average Taper Air Gap | DTA | 0.06 | m
Main Air Gap Proportion | Pm | 0.5 | (-)
Taper Air Gap Proportion | Pt | 0.129 | (-)
Þ Salient Pole Factor | Ps = Pm + Pt x (DAG/DTA) | 0.5645 | (-)
Air dielectric constant | K | 1 | (-)
Number of Stator Slots | NS | 72 | (-)
Stator Slot Width | WSL | 0.0213 | m
Þ Stator slot area | AS = L1 x WSL | 0.024921 | m2
Stator Wedge Thickness | W | 0.009 | m
Coil Ground Wall Thickness (or include with W) | DGW | 0 | m
Dielectric Constant of Combined Wedge + Ground Wall | KW | 4 | (-)
Stator to Frame Capacitance (Factory Data, 3 phases) | CSF | 2.09e-07 | F
Stator common-mode voltage of the ASD output (From Drive supplier calculations or measurement.) | VCMVASD | 1590 | V
End effects multiplier on CSR (e.g. 5% from manufacturer) | Fend | 1.05 | (-)
Bearing and Insulation Data
Dielectric Constant of Oil | Ko | 3 | (-)
Bearing Length | Lb | 0.1757 | m
Bearing Diameter (ID) | D4 | 0.28 | m
Journal Diameter | D3 | 0.27966 | m
Number of Lobes | NL | 4 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | qp | 70.3 | degrees
Max/Min Shaft to Bearing Clearance Ratio This addresses shaft not running in center of bearing. | RC | 15 | (-)
Bearing insulation dielectric constant | Kbi | 2.1 | (-) |  | NOTE¾Not to scale.
Thickness of Bearing Insulation | Tbi | 0.0005 | m
Number of Insulating Strips | Nst | 2 | (-)
Shell Diameter (OD) | Dsh | 0.425 | m
Insulating Strip Width | Wst | 0.045 | m
Þ Area of Bearing Insulation | Abi = Nst x πDsh x Wst | 0.12017 | m2
Þ Bearing Factor | Bf = ½×NL×qp/360 × (RC+1/ RC ) | 5.8844 | (-)
Total Capacitance Drive end bonded | C = CAG + Cb + (Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.a)
Both shells bonded | C = CAG + 2 × Cb |  |  | Eqn. (G.2.b)
All shells floating | C = CAG + 2×(Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.c)
Air Gap Capacitance | CAG = 2πK × 8.85 × 10–12 × Ll/ln (D2/D1) |  |  | Eqn. (G.3)
Hydro-dynamic bearing capacitance | Cb = Bf × [2πKo × 8.85 × 10–12 × Lb/ln(D4/D3)] |  |  | Eqn. (G.5)
Bearing to frame insulation capacitance | Cbi = Kbi × 8.85 x 10 -12 x Abi /Tbi |  |  | Eqn. (G.7)
Stator to rotor capacitance | CSR = Fend x PS x [NS × AS × 8.85 × 10-12/(DAG× K +(W + DGW) × KW)] |  |  | Eqn. (G.9)
Common-mode Voltage Ratio | CMVR = (CSR + C)/CSR |  |  | Eqn. (G.10)
Peak Shaft Voltage | Vsh = VCMVASD /CMVR |  |  | Eqn. (G.11)
Discharge Energy | E = ½CVsh2 |  |  | Eqn. (G.1)
Figure G.5—Proportion of the rotor circumference where there is actually a gap, Ps
All items below this line are calculated from above inputs
AIR GAP CAPACITANCE CAG
Rotor Length: | 1.17 | m
Rotor Diameter: | 1.35 | m
Air Gap: | 0.03 | m
Air Dielectric Constant | 1 | (-)
CAPACITANCE: CAG | 1.4961e-09 | F
Dimensions for many commonly used bearings may be found in DIN Standard 31698
HYDRO-DYNAMIC BEARING CAPACITANCES, Cb and Cbi
Shaft to Babbit CB |  |  |  | Bearing to Frame Cbi
Babbit Length | 0.1757 | m |  | Shell OD: | 0.425 | m
Babbit ID | 0.28 | m |  | Circumference | 1.3352 | m
Journal Diameter | 0.27966 | m |  | Insulating strips width | 0.045 | m
Bearing Clearance | 0.00034 | m diametrical |  | Strip thickness | 0.0005 | m
Lobes | 4 | (-) |  | Number of Strips | 2 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | 70.3 | degrees |  | Dielectric Constant | 2.1 | (-)
Dielectric Constant of Oil | 3 | (-)
Ratio | 0.78111 | (-)
Max/min clearance ratio. This addresses shaft not running in center of bearing. | 15 | (-) |  | Shaft to housing, shell floating capacitance: | 4.3303e-09 | F
Shaft to Babbitt CB | 1.4194e-07 | F |  | Cbi (per bearing) Addresses insulation between bearing shell and bracket. | 4.4666e-09 | F
STATOR TO ROTOR CAPACITANCE, CSR
Air Gap | 0.03 | m |  | Stator Circumference | 4.4296 | m
Air Dielectric Constant | 1 | (-) |  | Slot Width | 0.0213 | m
Stator ID | 1.41 | m |  | Slot Area | 0.024921 | m2
Number Slots | 72 | (-) |  | Capacitance per slot | 3.3417e-12 | F
Wedge plus Ground Wall | 0.009 | m |  | Stator/rotor Capacitance | 1.3582e-10 | F
Wall Dielectric Constant | 4 | (-) |  | Stator end effects multiplier on CSR | 1.05 | (-)
Stator Length | 1.17 | m |  | CSR | 1.4261e-10 | F
Portion under Pole | 0.5645 | (-)
Portion under Salient Pole Allowing for Edge Taper:
Location | Air gap | Proportion | Equivalent
Main | 0.03 | 0.5 | 0.5
Tapered | 0.06 | 0.129 | 0.0645
Equivalent portion |  |  | 0.5645
CAPACITANCE SUMMARY
CAG air gap | 1.4961e-09 | F
Cb shaft to bearing | 1.4194e-07 | F
Cbi bearing to frame | 4.4666e-09 | F
CSR stator to rotor | 1.4261e-10 | F
CSF stator to frame | 2.09e-07 | F
TOTAL CAPACITANCE, C
All shells floating C | 1.0157e-08 | F | 0.010157 | μF
DE shell bonded C | 1.4777e-07 | F | 0.14777 | μF
Both shells bonded C | 2.8539e-07 | F | 0.28539 | μF
SHAFT PEAK VOLTAGE AND DISCHARGE ENERGY
Voltages
Stator CMV, VCMVASD | 1590 | V pk
Shaft Peak Voltage, Vsh | 22.0161 | V pk | All floating
| 1.533 | V pk | DE bonded
| 0.79414 | V pk | Both bonded
Discharge Energy, E | 2.4615 | μJ | All floating
| 0.17364 | μJ | DE bonded
| 0.089991 | μJ | Both bonded
CMV Ratio, CMVR | 72.2199 | (--) | All floating
| 1037.1876 | (--) | DE bonded
| 2002.1554 | (--) | Both bonded
Table G.2 -
MIE and Group of flammable gases 54
|  |  |  | Chemical | MIE μJ | Division Group | Zone Group
|  |  |  | Methane | 280 | D | IIA
|  |  |  | Pentane | 280 | D | IIA
|  |  |  | Butane | 250 | D | IIA
|  |  |  | Propane | 250 | D | IIA
|  |  |  | Ethane | 240 | D | IIA
|  |  |  | Ethylene | 70 | C | IIB
|  |  |  | Hydrogen | 19 | B | IIC
|  |  |  | Acetylene | 17 | A | IIC
Table G.3 -
Maximum shaft voltage permitted with known total capacitance based on Capacitive ignition curves in Figure G.8
|  |  |  | Total capacitance, C | Flammable Gas or Vapor, Material Group
|  |  |  | (μF) | D or IIA | C or IIB | A and B or IIC
Minimum ignition voltage (V)
|  |  |  | 0.01 | 500 | 350 | 110
|  |  |  | 0.1 | 170 | 110 | 38.8
|  |  |  | 1 | 55 | 35 | 19.5
|  |  |  | 10 | 24.6 | 17 | 11.5
|  |  |  | 100 | 17 | 12 | 7
NOTE 1— Legend: 1 is total capacitance, C (μfarad); 2 is shaft voltage Vsh (volts).
Figure G.8- Capacitive ignition curves 55
55 IEC 60079-0 ed.7.0 [B47] Copyright © 2017 IEC Geneva, Switzerland. www.iec.ch
NOTE: For CSF, this capacitance bypasses some of the CMV energy away from the rotor to frame capacitance. CSF can be measured or calculated; however, it is generally not considered, which is a more conservative energy calculation.
Figure G.3 - Motor capacitance schematic, general
Figure G.6—Motor voltage schematic, general
Figure G.4—Examples of four-lobe (top) or cylindrical (bottom) bearings
54 Reproduced with permission of NFPA from NFPA 497 [B84], Recommended Practice for the Classification of Flammable Liquids, Gases or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas, 2017 edition. Copyright © 2016, National Fire Protection Association, Quincy, MA. This reprinted material is not the complete and official position of the NFPA on the reference subject, which is represented only by the standard in its entirety. For a full copy of NFPA 497, please go to nfpa.org.

## Synchronous Cylindrical Rotor
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
CAPACITANCE AND ENERGY CALCULATIONS |  |  |  |  | Metric Units
[5 empty] | Version 2021.0 | 2021-06-16
SYNCHRONOUS CYLINDRICAL MACHINE |  |  |  |  | REF:
MACHINE CAPACITANCES
Blue Highlighted cells are explanatory
Yellow Highlighted cells require data entry |  | OD = Outer diameter
Purple Highlighted cells are calculated answers |  | ID = Inner diameter
Stator and Rotor Data
Stator Length | L1 | 1.17 | m
Rotor Length | L2 (= L1 typically) | 1.17 | m
Rotor Diameter (OD) | D1 | 0.9 | m
Stator to Rotor Main Air Gap | DAG | 0.015 | m
Þ Stator diameter (ID) | D2 = D1 + 2DAG | 0.93 | m
Air dielectric constant | K | 1 | (-)
Number of Stator Slots | NS | 60 | (-)
Stator Slot Width | WSL | 0.018 | m
Þ Stator slot area | AS = L1 x WSL | 0.02106 | m2
Stator Wedge Thickness | W | 0.009 | m
Coil Ground Wall Thickness (or include with W) | DGW | 0 | m
Dielectric Constant of Combined Wedge + Ground Wall | KW | 4 | (-)
Stator to Frame Capacitance (Factory Data, 3 phases) | CSF | 1.5e-07 | F
Stator common-mode voltage of the ASD output (From Drive supplier calculations or measurement.) | VCMVASD | 1500 | V
Stator end effects multiplier on CSR (e.g. 5% from manufacturer) | Fend | 1.05 | (-)
Bearing and Insulation Data
Dielectric Constant of Oil | Ko | 3 | (-)
Bearing Length | Lb | 0.106 | m
Bearing Diameter (ID) | D4 | 0.16 | m
Journal Diameter | D3 | 0.1598 | m
Number of Lobes | NL | 4 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | qp | 90 | degrees
Max/Min Shaft to Bearing Clearance Ratio This addresses shaft not running in center of bearing. | RC | 15 | (-)
Bearing insulation dielectric constant | Kbi | 2.1 | (-) |  | NOTE¾Not to scale.
Thickness of Bearing Insulation | Tbi | 0.0005 | m
Number of Insulating Strips | Nst | 2 | (-)
Shell Diameter (OD) | Dsh | 0.3 | m
Insulating Strip Width | Wst | 0.045 | m
Þ Area of Bearing Insulation | Abi = Nst x πDsh x Wst | 0.084823 | m2
Þ Bearing Factor | Bf = ½×NL×qp/360 × (RC+1/ RC ) | 7.5333 | (-)
Total Capacitance Drive end bonded | C = CAG + Cb + (Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.a)
Both shells bonded | C = CAG + 2 × Cb |  |  | Eqn. (G.2.b)
All shells floating | C = CAG + 2×(Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.c)
Air Gap Capacitance | CAG = 2πK × 8.85 × 10–12 × Ll/ln (D2/D1) |  |  | Eqn. (G.3)
Hydro-dynamic bearing capacitance | Cb = Bf × [2πKo × 8.85 × 10–12 × Lb/ln(D4/D3)] |  |  | Eqn. (G.5)
Bearing to frame insulation capacitance | Cbi = Kbi × 8.85 x 10 -12 x Abi /Tbi |  |  | Eqn. (G.7)
Stator to rotor capacitance | CSR = Fend x [NS × AS × 8.85 × 10-12/(DAG× K +(W + DGW) × KW)] |  |  | Eqn. (G.8)
Common-mode Voltage Ratio | CMVR = (CSR + C)/CSR |  |  | Eqn. (G.10)
Peak Shaft Voltage | Vsh = VCMVASD /CMVR |  |  | Eqn. (G.11)
Discharge Energy | E = ½CVsh2 |  |  | Eqn. (G.1)
All items below this line are calculated from above inputs
AIR GAP CAPACITANCE CAG
Rotor Length: | 1.17 | m
Rotor Diameter: | 0.9 | m
Air Gap: | 0.015 | m
Air Dielectric Constant | 1 | (-)
CAPACITANCE: CAG | 1.9841e-09 | F
Dimensions for many commonly used bearings may be found in DIN Standard 31698
HYDRO-DYNAMIC BEARING CAPACITANCES, Cb and Cbi
Shaft to Babbit CB |  |  |  | Bearing to Frame Cbi
Babbit Length | 0.106 | m |  | Shell OD: | 0.3 | m
Babbit ID | 0.16 | m |  | Circumference | 0.94248 | m
Journal Diameter | 0.1598 | m |  | Insulating strips width | 0.045 | m
Bearing Clearance | 0.0002 | m diametrical |  | Strip thickness | 0.0005 | m
Lobes | 4 | (-) |  | Number of Strips | 2 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | 90 | degrees |  | Dielectric Constant | 2.1 | (-)
Dielectric Constant of Oil | 3 | (-)
Ratio | 1 | (-)
Max/min clearance ratio. This addresses shaft not running in center of bearing. | 15 | (-) |  | Shaft to housing, shell floating capacitance: | 3.0622e-09 | F
Shaft to Babbitt CB | 1.065e-07 | F |  | Cbi (per bearing) Addresses insulation between bearing shell and bracket. | 3.1529e-09 | F
STATOR TO ROTOR CAPACITANCE, CSR
Air Gap | 0.015 | m |  | Stator Circumference | 2.9217 | m
Air Dielectric Constant | 1 | (-) |  | Slot Width | 0.018 | m
Stator ID | 0.93 | m |  | Slot Area | 0.02106 | m2
Number Slots | 60 | (-) |  | Capacitance per slot | 3.6545e-12 | F
Wedge plus Ground Wall | 0.009 | m |  | Stator/rotor Capacitance | 2.1927e-10 | F
Wall Dielectric Constant | 4 | (-) |  | Stator end effects multiplier on CSR | 1.05 | (-)
Stator Length | 1.17 | m |  | CSR | 2.3024e-10 | F
CAPACITANCE SUMMARY
CAG air gap | 1.9841e-09 | F
Cb shaft to bearing | 1.065e-07 | F
Cbi bearing to frame | 3.1529e-09 | F
CSR stator to rotor | 2.3024e-10 | F
CSF stator to frame | 1.5e-07 | F
TOTAL CAPACITANCE, C
All shells floating C | 8.1085e-09 | F | 0.0081085 | μF
DE shell bonded C | 1.1154e-07 | F | 0.11154 | μF
Both shells bonded C | 2.1498e-07 | F | 0.21498 | μF
SHAFT PEAK VOLTAGE AND DISCHARGE ENERGY
Voltages
Stator CMV, VCMVASD | 1500 | V pk
Shaft Peak Voltage, Vsh | 41.4155 | V pk | All floating
| 3.0897 | V pk | DE bonded
| 1.6047 | V pk | Both bonded
Discharge Energy, E | 6.954 | μJ | All floating
| 0.53242 | μJ | DE bonded
| 0.2768 | μJ | Both bonded
CMV Ratio, CMVR | 36.2183 | (--) | All floating
| 485.4811 | (--) | DE bonded
| 934.7439 | (--) | Both bonded
Table G.2 -
MIE and Group of flammable gases 54
|  |  |  | Chemical | MIE μJ | Division Group | Zone Group
|  |  |  | Methane | 280 | D | IIA
|  |  |  | Pentane | 280 | D | IIA
|  |  |  | Butane | 250 | D | IIA
|  |  |  | Propane | 250 | D | IIA
|  |  |  | Ethane | 240 | D | IIA
|  |  |  | Ethylene | 70 | C | IIB
|  |  |  | Hydrogen | 19 | B | IIC
|  |  |  | Acetylene | 17 | A | IIC
Table G.3 -
Maximum shaft voltage permitted with known total capacitance based on Capacitive ignition curves in Figure G.8
|  |  |  | Total capacitance, C | Flammable Gas or Vapor, Material Group
|  |  |  | (μF) | D or IIA | C or IIB | A and B or IIC
Minimum ignition voltage (V)
|  |  |  | 0.01 | 500 | 350 | 110
|  |  |  | 0.1 | 170 | 110 | 38.8
|  |  |  | 1 | 55 | 35 | 19.5
|  |  |  | 10 | 24.6 | 17 | 11.5
|  |  |  | 100 | 17 | 12 | 7
NOTE 1— Legend: 1 is total capacitance, C (μfarad); 2 is shaft voltage Vsh (volts).
Figure G.8- Capacitive ignition curves 55
55 IEC 60079-0 ed.7.0 [B47] Copyright © 2017 IEC Geneva, Switzerland. www.iec.ch
NOTE: For CSF, this capacitance bypasses some of the CMV energy away from the rotor to frame capacitance. CSF can be measured or calculated; however, it is generally not considered, which is a more conservative energy calculation.
Figure G.3 - Motor capacitance schematic, general
Figure G.6—Motor voltage schematic, general
Figure G.4—Examples four-lobe (top) or cylindrical (bottom) bearings
54 Reproduced with permission of NFPA from NFPA 497 [B84], Recommended Practice for the Classification of Flammable Liquids, Gases or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas, 2017 edition. Copyright © 2016, National Fire Protection Association, Quincy, MA. This reprinted material is not the complete and official position of the NFPA on the reference subject, which is represented only by the standard in its entirety. For a full copy of NFPA 497, please go to nfpa.org.

## Induction Machine
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
CAPACITANCE AND ENERGY CALCULATIONS |  |  |  |  | Metric Units
[5 empty] | Version 2021.0 | 2021-06-16
INDUCTION MACHINE |  |  |  |  | REF:
MACHINE CAPACITANCES
Blue Highlighted cells are explanatory
Yellow Highlighted cells require data entry |  | OD = Outer diameter
Purple Highlighted cells are calculated answers |  | ID = Inner diameter
Stator and Rotor Data
Stator Length | L1 | 1 | m
Rotor Length | L2 (= L1 typically) | 1 | m
Rotor Diameter (OD) | D1 | 0.98 | m
Stator to Rotor Main Air Gap | DAG | 0.01 | m
Þ Stator diameter (ID) | D2 = D1 + 2DAG | 1 | m
Air dielectric constant | K | 1 | (-)
Number of Stator Slots | NS | 60 | (-)
Stator Slot Width | WSL | 0.015 | m
Þ Stator slot area | AS = L1 x WSL | 0.015 | m2
Stator Wedge Thickness | W | 0.009 | m
Coil Ground Wall Thickness (or include with W) | DGW | 0 | m
Dielectric Constant of Combined Wedge + Ground Wall | KW | 4 | (-)
Stator to Frame Capacitance (Factory Data, 3 phases) | CSF | 1.5e-07 | F
Stator common-mode voltage of the ASD output (From Drive supplier calculations or measurement.) | VCMVASD | 500 | V
Stator end effects multiplier on CSR (e.g. 5% from manufacturer) | Fend | 1 | (-)
Bearing and Insulation Data
Dielectric Constant of Oil | Ko | 4 | (-)
Bearing Length | Lb | 0.0635 | m
Bearing Diameter (ID) | D4 | 0.15255 | m
Journal Diameter | D3 | 0.1524 | m
Number of Lobes | NL | 4 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | qp | 90 | degrees
Max/Min Shaft to Bearing Clearance Ratio This addresses shaft not running in center of bearing. | RC | 1 | (-)
Bearing insulation dielectric constant | Kbi | 2 | (-) |  | NOTE¾Not to scale.
Thickness of Bearing Insulation | Tbi | 0.0005 | m
Number of Insulating Strips | Nst | 2 | (-)
Shell Diameter (OD) | Dsh | 0.283 | m
Insulating Strip Width | Wst | 0.045 | m
Þ Area of Bearing Insulation | Abi = Nst x πDsh x Wst | 0.080016 | m2
Þ Bearing Factor | Bf = ½×NL×qp/360 × (RC+1/ RC ) | 1 | (-)
Total Capacitance Drive end bonded | C = CAG + Cb + (Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.a)
Both shells bonded | C = CAG + 2 × Cb |  |  | Eqn. (G.2.b)
All shells floating | C = CAG + 2×(Cb × Cbi)/(Cb + Cbi) |  |  | Eqn. (G.2.c)
Air Gap Capacitance | CAG = 2πK × 8.85 × 10–12 × Ll/ln (D2/D1) |  |  | Eqn. (G.3)
Hydro-dynamic bearing capacitance | Cb = Bf × [2πKo × 8.85 × 10–12 × Lb/ln(D4/D3)] |  |  | Eqn. (G.5)
Bearing to frame insulation capacitance | Cbi = Kbi × 8.85 x 10 -12 x Abi /Tbi |  |  | Eqn. (G.7)
Stator to rotor capacitance | CSR = Fend x [NS × AS × 8.85 × 10-12/(DAG× K +(W + DGW) × KW)] |  |  | Eqn. (G.8)
Common-mode Voltage Ratio | CMVR = (CSR + C)/CSR |  |  | Eqn. (G.10)
Peak Shaft Voltage | Vsh = VCMVASD /CMVR |  |  | Eqn. (G.11)
Discharge Energy | E = ½CVsh2 |  |  | Eqn. (G.1)
All items below this line are calculated from above inputs
AIR GAP CAPACITANCE CAG
Rotor Length: | 1 | m
Rotor Diameter: | 0.98 | m
Air Gap: | 0.01 | m
Air Dielectric Constant | 1 | (-)
CAPACITANCE: CAG | 2.7523e-09 | F
Dimensions for many commonly used bearings may be found in DIN Standard 31698
HYDRO-DYNAMIC BEARING CAPACITANCES, Cb and Cbi
Shaft to Babbit CB |  |  |  | Bearing to Frame Cbi
Babbit Length | 0.0635 | m |  | Shell OD: | 0.283 | m
Babbit ID | 0.15255 | m |  | Circumference | 0.88907 | m
Journal Diameter | 0.1524 | m |  | Insulating strips width | 0.045 | m
Bearing Clearance | 0.00015 | m diametrical |  | Strip thickness | 0.0005 | m
Lobes | 4 | (-) |  | Number of Strips | 2 | (-)
Pad arc For cylindrical bearing make pad arc x number lobes = 360 | 90 | degrees |  | Dielectric Constant | 2 | (-)
Dielectric Constant of Oil | 4 | (-)
Ratio | 1 | (-)
Max/min clearance ratio. This addresses shaft not running in center of bearing. | 1 | (-) |  | Shaft to housing, shell floating capacitance: | 2.3658e-09 | F
Shaft to Babbitt CB | 1.4357e-08 | F |  | Cbi (per bearing) Addresses insulation between bearing shell and bracket. | 2.8326e-09 | F
STATOR TO ROTOR CAPACITANCE, CSR
Air Gap | 0.01 | m |  | Stator Circumference | 3.1416 | m
Air Dielectric Constant | 1 | (-) |  | Slot Width | 0.015 | m
Stator ID | 1 | m |  | Slot Area | 0.015 | m2
Number Slots | 60 | (-) |  | Capacitance per slot | 2.8859e-12 | F
Wedge plus Ground Wall | 0.009 | m |  | Stator/rotor Capacitance | 1.7315e-10 | F
Wall Dielectric Constant | 4 | (-) |  | Stator end effects multiplier on CSR | 1 | (-)
Stator Length | 1 | m |  | CSR | 1.7315e-10 | F
CAPACITANCE SUMMARY
CAG air gap | 2.7523e-09 | F
Cb shaft to bearing | 1.4357e-08 | F
Cbi bearing to frame | 2.8326e-09 | F
CSR stator to rotor | 1.7315e-10 | F
CSF stator to frame | 1.5e-07 | F
TOTAL CAPACITANCE, C
All shells floating C | 7.4839e-09 | F | 0.0074839 | μF
DE shell bonded C | 1.9475e-08 | F | 0.019475 | μF
Both shells bonded C | 3.1466e-08 | F | 0.031466 | μF
SHAFT PEAK VOLTAGE AND DISCHARGE ENERGY
Voltages
Stator CMV, VCMVASD | 500 | V pk
Shaft Peak Voltage, Vsh | 11.3067 | V pk | All floating
| 4.4064 | V pk | DE bonded
| 2.7364 | V pk | Both bonded
Discharge Energy, E | 0.47838 | μJ | All floating
| 0.18906 | μJ | DE bonded
| 0.11781 | μJ | Both bonded
CMV Ratio, CMVR | 44.2217 | (--) | All floating
| 113.4717 | (--) | DE bonded
| 182.7218 | (--) | Both bonded
Table G.2 -
MIE and Group of flammable gases 54
|  |  |  | Chemical | MIE μJ | Division Group | Zone Group
|  |  |  | Methane | 280 | D | IIA
|  |  |  | Pentane | 280 | D | IIA
|  |  |  | Butane | 250 | D | IIA
|  |  |  | Propane | 250 | D | IIA
|  |  |  | Ethane | 240 | D | IIA
|  |  |  | Ethylene | 70 | C | IIB
|  |  |  | Hydrogen | 19 | B | IIC
|  |  |  | Acetylene | 17 | A | IIC
Table G.3 -
Maximum shaft voltage permitted with known total capacitance based on Capacitive ignition curves in Figure G.8
|  |  |  | Total capacitance, C | Flammable Gas or Vapor, Material Group
|  |  |  | (μF) | D or IIA | C or IIB | A and B or IIC
Minimum ignition voltage (V)
|  |  |  | 0.01 | 500 | 350 | 110
|  |  |  | 0.1 | 170 | 110 | 38.8
|  |  |  | 1 | 55 | 35 | 19.5
|  |  |  | 10 | 24.6 | 17 | 11.5
|  |  |  | 100 | 17 | 12 | 7
NOTE 1— Legend: 1 is total capacitance, C (μfarad); 2 is shaft voltage Vsh (volts).
Figure G.8- Capacitive ignition curves 55
55 IEC 60079-0 ed.7.0 [B47] Copyright © 2017 IEC Geneva, Switzerland. www.iec.ch
NOTE: For CSF, this capacitance bypasses some of the CMV energy away from the rotor to frame capacitance. CSF can be measured or calculated; however, it is generally not considered, which is a more conservative energy calculation.
Figure G.3 - Motor capacitance schematic, general
Figure G.6—Motor voltage schematic, general
Figure G.4—Examples of four-lobe (top) or cylindrical (bottom) bearings
54 Reproduced with permission of NFPA from NFPA 497 [B84], Recommended Practice for the Classification of Flammable Liquids, Gases or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas, 2017 edition. Copyright © 2016, National Fire Protection Association, Quincy, MA. This reprinted material is not the complete and official position of the NFPA on the reference subject, which is represented only by the standard in its entirety. For a full copy of NFPA 497, please go to nfpa.org.

## NEMA frame ball bearings
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
CAPACITANCE AND ENERGY CALCULATIONS | [7 empty] | Metric Units
[8 empty] | Version 2021.0 |  | 2021-06-16
INDUCTION MACHINE | [7 empty] | REF:
INCENDIVE ENERGY ON ASD DRIVEN BALL BEARING MACHINES
IEEE Std 841, 4 pole motors to 500 HP on PWM ASD
REF: IEEE IAS Paper "System Electrical Parameters and Their Effects on Bearing Currents" [B19]
Table G.5—Discharge energy due to CMV for anti friction (ball) bearing motors, typical four-pole motor [B19]
MOTOR RATING (HP) | 5 |  | 15 |  | 50 |  | 90 |  | 375 |  | 500
VASD (V) | 480 | 600 | 480 | 600 | 480 | 600 | 480 | 600 | 480 | 600 | 480 | 600
BVR a | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.09 | 0.12 | 0.12 | 0.13 | 0.13 | 0.13 | 0.13
VCMVASD (V) b | 648 | 810 | 648 | 810 | 648 | 810 | 648 | 810 | 648 | 810 | 648 | 810
Vsh (V) d | 64.8 | 81 | 58.32 | 72.9 | 58.32 | 72.9 | 77.76 | 97.2 | 84.24 | 105.3 | 84.24 | 105.3
C (μF) c, d (both bearings bonded) | 0.001 | 0.001 | 0.0011 | 0.0011 | 0.0015 | 0.0015 | 0.0015 | 0.0015 | 0.005 | 0.005 | 0.005 | 0.005
E (μJ) e | 2.0995 | 3.2805 | 1.8707 | 2.9229 | 2.5509 | 3.9858 | 4.535 | 7.0859 | 17.7409 | 27.7202 | 17.7409 | 27.7202
Table G.2 -
MIE and Group of flammable gases 54
[8 empty] | Chemical | MIE μJ | Division Group | Zone Group
[8 empty] | Methane | 280 | D | IIA
[8 empty] | Pentane | 280 | D | IIA
[8 empty] | Butane | 250 | D | IIA
[8 empty] | Propane | 250 | D | IIA
[8 empty] | Ethane | 240 | D | IIA
[8 empty] | Ethylene | 70 | C | IIB
[8 empty] | Hydrogen | 19 | B | IIC
[8 empty] | Acetylene | 17 | A | IIC
Table G.3 -
Maximum shaft voltage permitted with known total capacitance based on Capacitive ignition curves in Figure G.8
[7 empty] | Total capacitance, C |  | Flammable Gas or Vapor, Material Group
[7 empty] | (μF) |  | D or IIA |  | C or IIB |  | A and B or IIC
Minimum ignition voltage (V)
[7 empty] | 0.01 |  | 500 |  | 350 |  | 110
[7 empty] | 0.1 |  | 170 |  | 110 |  | 38.8
[7 empty] | 1 |  | 55 |  | 35 |  | 19.5
[7 empty] | 10 |  | 24.6 |  | 17 |  | 11.5
[7 empty] | 100 |  | 17 |  | 12 |  | 7
NOTE 1— Legend: 1 is total capacitance, C (μfarad); 2 is shaft voltage Vsh (volts).
Figure G.8- Capacitive ignition curves 55
55 IEC 60079-0 ed.7.0 [B47] Copyright © 2017 IEC Geneva, Switzerland. www.iec.ch
a BVR is from Figure 5 of [B19]. BVR is the reciprocal of Common-Mode Voltage Ratio (CMVR) used in G.3.5 to calculate discharge energy, E.
b ASD output VCMVASD is half of the dc bus voltage. The reflection voltage is double this value; or, 1.35 x VASD.
c Total Capacitance, C, is from Figure 4 of [B19].
d Because the capacitance is not on the ignition curve chart, comparison of Vsh and C with the capacitive ignition curves in Figure G.8 and Table G.3 is not useful. The MIE should instead be calculated and compared to the lowest MIE of the flammable materials expected to be present.
e Calculate the discharge energy, E, using Equation (G.1) and compare to the MIE in Table G.2.
In Table G.5
VASD is the ASD input voltage (volts)
BVR is the bearing voltage ratio
VCMVASD is the common-mode voltage of the ASD output (volts)
Vsh is the peak shaft voltage (volts)
C is the total capacitance, sum of all capacitances of the rotor to the frame including the bearings across which the voltage, Vsh appears (farads)
E is the discharge energy (joules)
54 Reproduced with permission of NFPA from NFPA 497 [B84], Recommended Practice for the Classification of Flammable Liquids, Gases or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas, 2017 edition. Copyright © 2016, National Fire Protection Association, Quincy, MA. This reprinted material is not the complete and official position of the NFPA on the reference subject, which is represented only by the standard in its entirety. For a full copy of NFPA 497, please go to nfpa.org.

## Abbreviations & References
IEEE STD 1349-2021 DISCHARGE ENERGY CALCULATOR
Abbreviations
DE | Drive end
NDE | Non-drive end
ID | Inner diameter
OD | Outer diameter
E | is discharge energy (joules)
C | is total capacitance, sum of all capacitances of the rotor to the frame including the bearings across which the voltage, Vsh appears (farads)
Vsh | is peak shaft voltage (volts)
Cb | is capacitance between the shaft and the bearing at each end, with lubricant as the dielectric. (farads)
Cbi | is capacitance of the bearing to frame insulation (if any). (farads) This capacitance is often bypassed at one or both ends by a bonding jumper.
CAG | is capacitance across the air gap between the rotor and the stator laminations. (farads)
CSR | is capacitance between the stator winding and the rotor. (farads)
CSF | is three-phase capacitance between the stator winding and frame. (farads)
CMV | common-mode voltage (volts)
CMVR | common-mode voltage ratio
VCMVASD | common-mode voltage of the ASD output (volts)
Ll | is stator iron length (meters)
L2 | is rotor length (=L1 typically) (meters)
D1 | is rotor OD (meters)
D2 | is stator ID (meters)
DAG | is stator to rotor main air gap (meters)
DTA | is stator to rotor average taper air gap (meters)
Pm | is main air gap proportion
Pt | is taper air gap proportion
PS | is salient-pole factor
K | is dielectric constant (air = 1)
NS | is the number of stator slots
WSL | is stator slot width (m)
AS | is the stator slot area given as (length x width) (meters2)
W | is the stator wedge thickness (meters)
DGW | is the coil ground wall thickness (meters)
K W | is a dielectric constant of combined wedge plus ground wall
Fend | is stator end effects multiplier on CSR. See Note 1. NOTE 1-The IEEE 1349 Calculator add 5% to CSR to account for end effects as provided by the manufacturer
Ko | is dielectric constant of oil (taken as 3 or 4 in examples, actual figure is about 2.5)
Lb | is bearing length (of Babbitt) (meters)
D3 | is journal diameter (meters)
D4 | is bearing ID (meters)
NL | is Number of Lobes
qp | is Pad Arc, degrees For cylindrical bearing make pad arc x number lobes = 360 degrees.
RC | Max/Min Shaft to Bearing Clearance Ratio This addresses shaft not running in center of bearing.
Kbi | is bearing insulation dielectric constant
Tbi | is thickness of bearing insulation (m)
Nst | is number of insulating strips
Dsh | is shell diameter, outside diameter (m)
Wst | is insulating strip width (m)
Abi | is area of bearing insulation (m2)
Bf | is bearing factor (This addresses the shaft not running in the center of the bearing (RC term) and the active portion of the bearing circumference (NL × qp / 360).
References (Informative)
[B19] | Busse, Erdman, Kerkman, Schlegel, Skibinski, “System Electrical Parameters and Their Effects on Bearing Currents,” IEEE Transactions on Industry Applications, vol. 33, no. 2, pp 577-584, March/April 1997
[B33] | DIN Standard 31698-1979, Plain Bearings, Fits, DIN e. V., Budapester Straße 31, 10787, Berlin, Germany.
[B47] | IEC 60079-0:2017 Explosive Atmospheres - Part 0: Equipment - General Requirements
[B72] | Mistry, B., B. Lockley, and D.Ankele, "Shaft-Bonding Devices: Application on Large Inverter-Fed Machines Operating in a Class 1 Location," in IEEE Industry Applications Magazine, vol. 25, no. 6, pp. 16-24, Nov.-Dec. 2019, doi: 10.1109/MIAS.2018.2875192.
[B76] | Muetze, A. and Binder, Andreas, “Calculation of Motor Capacitances for Prediction of the Voltage Across the Bearings in Machines of Inverter-Based Drive Systems, IEEE Transactions on Industry Applications, vol. 43, no. 3, pp 665 - 672, DOI: 10.1109/TIA.2007.895734.
[B84] | NFPA 497-2017, Recommended Practice for the Classification of Flammable Liquids, Gases, or Vapors and of Hazardous (Classified) Locations for Electrical Installations in Chemical Process Areas