Date: 04/16/98

To: ADSCOM Sub-committee IEEE Switchgear

From: Pete Dwyer

Subject: C37.59 Meeting 5 May 98 at Ft Lauderdale Switchgear series

A meeting of the W/G was carried out between 2pm and 6pm  on May 5. The W/G

membership was revised to reflect present interested parties of six

manufacturers, two consultant and one users. A number of other people

requested to be included for comments as part of the W/G process.

Based on the ADSCOM decision to include conversions associated with

installation of contactors in switchgear, Alan Storms, a representative of

Low Voltage Devices, will prepare and distribute an outline of documentation

planned for LVD and also a tabulation of specific subjects related to this

type of conversions which should be considered for C37.59. These will be E

Mailed in one month to those with E Mail capability.

A number of additional definitions are to be drafted by Ted Burse and Albert

Livshitz and distributed by E Mail within one month. The intent is to reduce

confusion that has been reported. These will include: Contactor Conversion,

Retrofill Breaker, Replacement Breaker, Cell Conversion, Design Verified

Component.

There was much discussion concerning MOC compatibility with the mechanism,

particularly when vacuum breaker modules are substituted for air-magnetic

modules. The existing C37.59 does warn of concerns and that possibly the

best conversion reliability would include changing of the MOCs. It was

agreed to leave the endurance test requirements to the “between servicing

limits” as is in the present standard. In an attempt to strengthen this

area, Pete Dwyer will prepare and E Mail (in one month) text changes

suggested for the annex to provide a typical process to be considered for

the compatibility. The suggested format for design verification of the total

conversion will also be changed to reflect the need for additional

information and suggestions will be included for a users examination of a

particular design. In such a complex issue as this compatibility, the

expertise of the converter

The HVCB Sub-committee suggested that the ADSCOM decision on contactor

conversions should include not only low but also high voltage devices. It

was also stated that we should be sure to include or reference the meaning

of voltage levels.

The previously submitted PAR apparently was lost in the system. I will

regenerate it.

Member or Guest / Contact  Listing:

Pete Dwyer       M(chair)  GE

Alan D Storms M Consultant

Harpinder S Gill   M  Schneider Canada  gillh@squared.com

Miklos J Orosz M Square D     615-459-1334       oroszm@squared.com

Dennis R Thonsgard    Powell        G     713-947-1334

dthonsga@powl.com

Ted A Burse Powell  M tburse@powl.com

Albert Livshitz    PDS M 513-755-4854  al@pdspower.com

Rick Jackson Detroit Edison M 313-235-3856 jacksonr@detroitedison.com

Larry Schmidt Square D M 615-459-8466

Dean Sigmon ABB  G

William M Bradley M Commonwealth Edison 708-410-7952

Ward Laubach M Consultant

Bob Puckett M Dupont

Gerry Sakats M Powecon

Wally Marcus I Dresdan Power Plant

Nigel P McQuin I Consultant

Keith Gray I Consultant

Paul J Notarian	I

Pete