IEEE Switchgear Committee

Low Voltage Switchgear Devices Subcommittee

May 10, 2000

C37.26-1972

Review of document – need for revisions

The status of the document is as follows:

| Number | Title | IEEE Status | ANSI Status | Contact |
| --- | --- | --- | --- | --- |
| C37.26 | Guide for Methods of Power Factor Measurements for Low Voltage Inductive Test Circuits | App 9-71 Reaff 9-77 Reaff 9-90 Reaff 12-96 | App 5-72 Reaff 6-86 Reaff 2-91 Reaff 7-97 | H. L. Hess (215)-340-7547 hlhgator55@erols.com |

Reaffirmation is required in 2001.  Considering that the document will observe its 30th birthday in 2001, should we consider revising the document?

Discussion points:

- The document is considered to represent current practice and is, therefore, “state-of-the-art”.

- Metrification is unnecessary, as the only units used in the document are already metric.

- C37.26 is referenced in a variety of documents, including C37.20.1, C37.50, C37.51, C37.52, C37.57, and perhaps others.

- Except for modernization of format and presentation, there is no pressing need for revision.

- There is a need for a guide to determine time constants for dc testing, particularly in laboratory systems in which a dc generator is not available and the dc source is actually rectification of ac power.  However, extension to the dc area would extend the scope.

- There is a need for more guidance on conducting a variety of laboratory tests (shielding of leads, data acquisition, interference, etc.) but these issues are outside the scope of this document.  If these issues are pursued, a different document (perhaps a guide or recommended practice or tutorial) is probably appropriate.

- Recommendations:

- Reaffirm in 2001

- Do not (at this time) form a working group to revise the document

- Consider forming a task force (TF) to consider the need for a guide for determination of time constants during dc short-circuit testing, and to consider other testing issues (e.g., power loss determinations for metal-enclosed bus).  If formed, the TF should determine if this subject fits under a different group (e.g., PSIM, the rectifier group), whether IEC has a document which deals with the issue, recommend whether the scope of C37.26 (or C37.14) should be changed and the document revised, determine if these issues are better covered in a separate document.

- Conclusions by the LVSD Subcommittee:

- Reaffirm C37.26 in 2001.

- Recommend that Switchgear Assemblies (and C37.23) consider covering power loss determination.

- N. McQuin will evaluate will evaluate the issue of dc time constants for rectified dc systems further, and will report in the Fall 2000 meeting.

Summarized by:  T. W. Olsen