# Proposal for New Work Item

Joint Investigation by the Transformer Committee and the Switchgear Committee to determine what design factors in the development of a transformer design lead to natural frequencies greater than (to be determined) kHz when viewed from the high side with the low side shorted.  How is this related to voltage rating and to the MVA size and type of construction used to build the transformer?  We are finding more and more applications of this type. A fault on the low side or opposite side of a transformer may well be within the interrupting rating of the breaker but the breaker may not properly interrupt this fault because the transient recovery voltage frequency is too great.  We know that the form of the recovery voltage will be a 1 – cosine waveshape with peak amplitude around twice the peak line to neutral voltage. Depending on the rated voltage and the frequency of oscillation the recovery voltage may be beyond the capability of most standard breakers of a given class and at the same time the fault current level is well within the interrupting rating of the breaker.

# Discussion

There is very little hard data on this paradox other than the Harner /Rodriquez paper IEEE Transactions PAS 1972 Sept/Oct pages 1887-1869.  This paper looked at 117 transformer installations of different voltage classes and MVA ratings.  Less than 50 of these units were for voltages 46 kV and above. By the method of current injection the authors were able to predict the recovery voltage of these installations.  Based on this data they made assumptions on how the recovery voltage may vary as a function of voltage rating and MVA size.  As an industry we are trying to extend this data into a rating structure which may or may not be valid. What we do know is that there have been failures of breakers and damage to other equipment as a result of these phenomena.

At the present time neither ANSI/IEEE or IEC Standards properly address this issue. The ANSI Standard C37.06.1 1997 provided some trial use recommendations for tests and ratings of a class of definite purpose breakers (this standard has now been adopted without significant modifications or test experience).  This rating structure was created from engineering judgment of the situation.  It may or may not be adequate for the task.  What is sure is that the rates of rise of recovery voltage given still do not cover some applications and the times to peak are so fast that synthetic circuits must be used in most development testing.

During the factory QA test program most transformers are injected with a fast front high voltage impulse type (typically a 1.2x50 microsecond) wave which is used to establish the internal condition of the transformer before testing. This process is repeated after testing to assure that the testing has not damaged the transformer.  This test is also used as a record to determine if damage has occurred due to a through fault later in the life of the transformer. Among the tests done are a measurement of impedance between the various windings and a measurement of the capacitance from the various terminals with other terminals open or grounded.  However, this data does not provide the natural ringing frequency to be expected during a short circuit.  This means that the data we desire typically is not being measured or recorded.  Although most of the required setup to make such a measurement is being used.

Beyond this to do a complete investigation we need help from the Transformer Committee in cataloging the data and trying to reconcile the driving factors that lead to the very fast recovery voltages.  Are economical alternate designs available that would avoid this problem? Is this just a matter of informing the transformer designer? Is this the result of typical design of certain types of transformers? Dry type transformers as an example. Will this be true for all voltage ratings? What problems do the transformer designers see in adding capacitance at the terminals of the transformer?  We should be able to develop a L*C value as a gauge equal to or less than some number (where L is in henries and C is in farads) which defines a transformer design that does not cause a problem.

If we can develop answers to these questions and quantify the conditions that lead to the need for special breakers in certain applications we would be able to inform the application engineers when to be on alert. This may save the industry money by developing and testing only those ratings that are required. The situation we are in at the moment is that the breaker manufacturers will be testing breakers for ratings that may not be the most needed values.  We lack experience to show that the values given in C37.06.1 2000 provide adequate coverage by voltage class for most applications.

The data that we need can be developed using any one of several methods currently being used in the process of testing transformers. The inductance required is the transformer leakage impedance, which is always recorded at the time of testing now. The measurement that we need that is not currently being done is to determine the transformer effective capacitance. This is a distributed capacitance across the winding, between windings and from the windings to ground. It is this capacitance when combined with the transformer leakage inductance that determines the frequency of the circuit breaker recovery voltage for a fault on the secondary side of the transformer.

Commercially available measurement systems such as FRAMIT based on frequency response analysis can be used. This system is primarily used to detect small physical distortions in the transformer winding. It can be used to determine the recovery voltage by lowering the search frequency to determine the primary frequencies of oscillation. Doble Engineering has recently developed a Sweep Frequency Analyzer M5100 that could also be used for this purpose. In addition bench top circuits as shown below can also be used for this purpose.

CIRCUITS USED TO DETERMINE NATURAL

FREQUENCY OF TRANSFORMER

HV

LV

SCOPE

3X 0-400 V

Current Injection Circuit

# Signal Generator Circuit

HV

LV

Resistor value large relative to leakage impedance

SCOPE

0 100 kHz

We would like to request that the transformer manufacturers routinely make such measurements and publish this information as a part of the test report for each transformer that they build. It seems that most manufacturers already have the equipment to do this test but at this time are not making this specific measurement. If we collect such data it will be easy for the user to identify those special cases where additional capacitance is needed and this can be added at the time of installation. A collection of this data will give standards writing organizations confidence that the standards properly reflect current practice.

In all of the above discussion we have not mentioned the voltage distribution across, between and to ground of windings that may be associated with switching the transformer. It is our understanding that the Transformer Committee already has a working group addressing problems of this type.

Mel Smith

May 8, 2001