Common Clause TF on Capacitance Current Switching

Under ADSCOM

Notes of interest  10/3/2001 meeting

A joint meeting was held with the HVCB WG on  Capacitance Current Switching (C37.04a &C37.09a) on October 3, 2001 In Quebec, QC with 14 members and 11 guests.

Roy Agreed to extract portions of C37.04a and C37.09a AND include appropriate clauses from IEEE 1247, to use as basis for a capacitance current switching common clause document.    (proposed circulation of document 1/15/2002)

A discussion was held on the value of  power quality enhancements to present standards.  No consensus reached.

Proposal:

Standards for controlled closing and   Limiting reignitions beyond 40 degrees

Performance measures

- no extraneous zero crossings produced during switching.

- Transient disturbance amplitude <0.3 p.u. voltage

- Inrush current , 0.3 p.u. of the theoretical maximum inrush current with no

Closing control (or a restrike at 90 degrees)

For Overhead line and cable switching this is to reduce overvoltages.

For capacitor banks this is to reduce overvoltages below 1.3 p.u.  and to  improve power quality by keeping capacitor switching transients low enough that

- there are no extraneous  voltage zero crossings:

- the magnitude and/or steepness of the voltage collapse are small enough to prevent  exciting resonances to dangerous levels.

Is there a need for such standards?

Some, including myself, think so.

My suggestions of the past few years cover this.

Others believe we should wait 10 years.  I think it may take that long to develop!

Grace & Peace

Roy Alexander