# C37.59 Revision	Minutes of April 30, 2002 Meeting			30 April 02

A meeting was held April 30, 2002 attended by 21 contributors. The purpose was to tabulate various suggestions for future consideration in C37.59 evolutions. The following were the results of the discussion:

Outline of New Work Suggestions for C37.59 (initiated at W/G Meeting 30 April 02)

- Paul Notarian – Relative to words in scope of document – some of UL had specific concerns Need specific concerns from Paul. Notarian. Response one month.

- Bob Puckett – L.V. Contactor conversions need specific reference. New document addresses fused contactor that can be made into an insertion unit for drawout gear. Need to be sure documents fit together. Also to be included as a reference document.

- Lots of discussion about latest content included on L.V. G&T. Concern about having no good solid ground system for LV  G&T. Must look hard at words to see if there is reality that it might inspire people to take risks. What is really going on in LV G&T? Nigel to check to see what is going on in labs.

- Recognize that someone may make a kit to “upgrade normal switchgear to 20.7 gear”. Apparently these already exist.

- Ratings of switchgear lineup with contactors in place of breakers – issues of  lower BIL and momentary, continuous current.

- Bob Puckett feels you have to assure that something is grounded on low voltage before working on it – he will look for reference. Others raised the issue of concern over the capacity and availability of ground connections for the available fault levels.

- C37.13 is being reviewed relative to the grounding requirements for front panels. Presently the grounding seemed pretty weak although it was pointed out that if the breaker faults to ground, the grounds cannot carry that level of current. (Doug Edwards)

It was requested of all attendees that they review copies of D21 attached to this memo and to send via E-Mail any areas of concern that appear to justify future action.

Pete Dwyer Chair W/G to revise C37.59