## IEEE Project PC37.59-20XX/ Draft 21

(Revision of IEEE Std C37.59-1996)

IEEE Draft Standard Requirements for

Conversion of Power Switchgear Equipment

Sponsor

Switchgear Committee

of the

IEEE Power Engineering Society

Approved YY

IEEE Standards Board

Abstract:  Directions and requirements are provided for the conversion of qualified power switchgear equipment. Examples such as low-voltage power circuit breakers; high-voltage outdoor and medium voltage indoor drawout  power circuit breakers; low and medium voltage fused contactors;  low and medium-voltage ground and test devices; medium voltage fused load interrupter switches; and all metal-enclosed switchgear are covered. Existing design standards are referenced with appropriate guidance on  design testing  necessary to design-verify the conversions. Reconditioning, which concerns the maintenance of existing equipment without alteration, is not covered.

Keywords: conversion, power switchgear equipment, qualified design

Copyright © <2002> by the Institute of Electrical and Electronics

Engineers, Inc.

3 Park Avenue

New York, NY 10016-5997, USA

All rights reserved.

This is an unapproved draft of a proposed IEEE Standard, subject to change. Permission is hereby granted for IEEE Standards Committee participants to reproduce this document for

purposes of IEEE standardization activities. If this document is to be submitted to ISO or

IEC, notification shall be given to the IEEE Copyright Administrator

Permission is also granted for member bodies and technical committees of ISO and IEC to

reproduce this document for purposes of developing a national position. Other entities seeking

permission to reproduce portions of this document for these or other uses must contact

the IEEE Standards Department for the appropriate license. IEEE is the sole entity that may

authorize the use of certification marks, trademarks, or other designations to indicate

compliance with the materials set forth herein. Use of information contained in the unapproved

draft is at your own risk.

IEEE Standards Department

Copyright and Permissions

445 Hoes Lane, P.O. Box 1331

Piscataway, NJ 08855-1331, USA

Introduction

(This introduction is not a part of ANSI/IEEE C37.59-20xx, IEEE Draft Standard Requirements for Conversion of Power Switchgear Equipment.)

This revised standard covers conversions of power switchgear equipment only, rather than a complete  power switchgear equipment replacement. A conversion of power switchgear equipment reuses some portion of the qualified design  switchgear.

This standard has been revised to correct some specific reference errors; to separate low-voltage and medium-voltage conversions for clarity; to include low and medium-voltage ground and test (G&T) devices; to clarify nameplate modification and additions; to include conversion of low and medium voltage circuit breakers to alternating current fused contactors and  conversion of interrupter switchgear to add or substitute power fuses. It has also been revised  to stress the importance of drawout interlocking and auxiliary functions known to have caused field problems.

Converted circuit breakers may or may not be interchangeable with existing non-converted circuit breakers. Where converted circuit breakers are not interchangeable with non-converted circuit breakers, it will be so indicated in the  converter’s instruction book and the blocking/rejection interlock shall be changed.

It is stressed that at least the minimum tests recommended and outlined in specific references are to be carried out as applicable on each differing design (or model) of a converted device. Reliance only on production tests with statements that the conversion has been “ANSI tested”, unsubstantiated by formal documented design verification, can mislead users and may result in field failures. Production tests are not design tests. The basic and fundamental philosophy of this standard is that a converted product is a new design and must be design verified to substantiate that it meets its nameplate ratings as well as applicable standards. A recommended design verification form is included.

The lack of design verification of some conversions was the reason for the creation of the original (1991) version of this document.  Experience gained with use of the original document and the 1996 revision has been incorporated into this revision of the standard.

There are many forms of conversion, and this document provides the logic that should cover all power switchgear  equipment conversions, with examples of current areas of conversion and testing. As additional types of switchgear products are converted, criteria for the new conversion products will be added in future revisions of this standard.

Annex A, though not a normative part of this standard, is provided for guidance in the design verification of the converted power switchgear equipment. It provides additional guidance regarding conversion examples and the minimum testing required for design verifications.

Examples of components that may be converted include but are not limited to:

Circuit breakers

- Frame

- Insulation structures

- Contacts, supports, and primary disconnecting devices

- High-voltage arc-interrupting structures

- Low-voltage arc-interrupting structures

- Note: This includes substitution of Low-voltage and medium-voltage  alternating current fused contactors in place of circuit breaker elements

- Low-voltage direct-acting trip device systems

- Drawout parts/interlocking and auxiliary functions

- Mechanism parts and control wiring

- Switchgear vertical sections

- Drawout parts/interlocking and auxiliary functions

- Frame

- Bus, bus connections, and insulation

- Instrumentation and control wiring

- Ground and Test devices

- Metal-enclosed interrupter switchgear

- Addition  or substitution of power fuses

This standard is not intended to cover maintenance procedures when reconditioning power switchgear equipment in accordance with the manufacturer’s instruction manuals.

The Administrative Subcommittee (ADSCOM) Working Group of the IEEE Switchgear Committee that prepared and approved this standard had the following membership:

P. W. Dwyer, Chair

Ted. A. Burse	Harpinger. S. Gill 	Ward. E. Laubach

Albert Livshitz	Nigel. P. McQuin	T. W. Olsen

Michael. Orosz 	Robert. J. Puckett	Gerald. Sakats

Keith I. Gray	Alan. D. Storms

Contents

1.	Overview

1.1	Scope

1.2	Other conversions

2.	References

2.1	Low-voltage equipment

2.2	Medium- and high-voltage equipment

2.3	Miscellaneous

3.	Definitions

4.	Service conditions

5.	Ratings

6.	Conversion and testing

6.1	Circuit breakers and related conversions

6.2	Switchgear vertical sections

6.3	Interrupter switchgear fuse conversions

7.	Production testing

8.	Nameplates

8.1	Individual interrupters

8.2	Modular assemblies

8.3	Others

9.	Manuals

10.	Recommended conversion design verification form

ANNEX

A	Clarification of conversion processes (Informative)

A.1	Introduction

A.2	Scope

A.3	Circuit breakers

A 4	Switchgear vertical sections

A 5	Additional MOC switch design verification

A6	Typical information to be documented for a conversion

IEEE Draft Standard Requirements for Conversion of Power Switchgear Equipment

1. Overview

This standard covers power switchgear equipment that is converted from a qualified design. It provides direction and guidance in those conversions and specifies required design verification in accordance with applicable ANSI, NEMA, UL, or IEEE standards.

This standard also recognizes that production/field testing does not provide design verification. This can only be accomplished by means of design testing and technical evaluation.

1.1 Scope

Present industry conversions involve low- and medium-voltage power circuit breakers used in metal-enclosed and metal-clad switchgear; low- and medium-voltage fused contactors; switchgear vertical sections; power fuse addition or substitution in metal-enclosed interrupter switchgear, and certain ratings of other  circuit breakers. This document outlines criteria for conversion of this type  of equipment.

This standard cannot detail each test that must be carried out to qualify a conversion. The specific tests shall be selected by the converter considering exact changes made from the previously qualified design. The converter shall conduct thorough and formal design verification for the completed conversion, and shall perform all additional tests determined to be necessary.

A vital part of the circuit breaker conversion process is the electrical and mechanical coordination of the mechanism-operated cell (MOC) switches with the converted circuit breaker to ensure proper operation. New, sealed interrupter, modular units may have much less mechanism power than that of the circuit breakers they replace, and  may not  have the ability to operate all installed MOC switches. Accordingly, this may necessitate substantial revision to or replacement of the MOC switches and their operating linkage in the existing vertical sections to assure proper operation.

Any conversions performed on third party labeled or listed equipment or equipment requiring Nuclear Regulatory Commission conformance  will void the label, listing, or certification of the equipment. It will be necessary to reapply to the third party for continued certification of the equipment. For instance typical examples are: if any UL listed   switchgear assembly is converted to use molded case circuit breakers in place of UL listed power circuit breakers, the converted switchgear assembly must be submitted to the UL, and  if a UL listed low-voltage power circuit breaker is converted to change the electro-mechanical series trip units to an electronic type trip unit, the converted breaker must be submitted to UL.

A converter shall not knowingly convert a design which he knows to be defective without taking or recommending appropriate action to correct the defect in any assembly being converted.

1.2 Other conversions

The conversion and testing processes outlined in this standard are based on known examples and are outlined for general guidance and direction. However, alterations can be made to other equipment,  not discussed  in detail in this document, that will require design verification in accordance with appropriate standards. Whenever there is any question, the converter should be consulted.

Additionally, while this standard specifically does not cover reconditioning of power switchgear equipment, it does recognize the process and the fact that appropriate production/field testing is necessary.

2. References

The following standards are referred to in this document and are the most recently published editions of the standards. When a standard is superseded by an approved revision, the revision shall apply.

However, when conversions are made to older total current rated circuit breakers, it is essential that the converted device ratings are correlated to at least meet the applicable ratings and design requirements of the original circuit breaker designs described in the appropriate edition of the standard.

2.1 Low-voltage equipment

ANSI C37.16-1997, Low-Voltage Power Circuit Breakers and AC Power Circuit Protectors -- Preferred Ratings, Related Requirements, and Application Recommendations.

ANSI C37.17-1997, Trip Devices for AC and General Purpose DC Low-Voltage Power Circuit Breakers.

ANSI C37.50-1989 (R1995),  Low-Voltage AC Power Circuit Breakers Used in Enclosures -- Test Procedures.

ANSI/IEEE C37.13-1990 (R1995), Low-Voltage AC Power Circuit Breakers Used in Enclosures

ANSI/IEEE C37.14-1999, Low-Voltage DC Power Circuit Breakers Used in Enclosures

ANSI/IEEE C37.20.1-19xx, Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear

ANSI C37.58 –1990 (R1997)  Indoor AC Medium-Voltage Switches for Use in Metal-Enclosed Switchgear- Conformance Test Procedures

NEMA ICS 2-1993, Industrial Control Devices

UL 508 (1993), Industrial  Control Equipment

ANSI/UL 489 (1991), Molded-Case Circuit Breakers and Circuit Breaker Enclosures

NFPA 70-1999 (National Electrical Code)

2.2 Medium- and high-voltage equipment

ANSI C37.06-2000, AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis -- Preferred Ratings and Related Required Capabilities.

ANSI/IEEE C37.04-1999,Rating Structure for AC High-Voltage Circuit Breakers ANSI/IEEE C37.09-1999,Test Procedure for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis.

ANSI/IEEE C37.20.2-1999, Metal-Clad  Switchgear

ANSI/IEEE C37.20.6-1997 ,Medium-Voltage Ground and Test Devices Used in Enclosures.

ANSI/IEEE C37.20.3-1987-2001, Metal-Enclosed Interrupter Switchgear

ANSI/IEEE C37.20.4-2000,  Indoor AC Medium-Voltage Switches for Use in Metal-Enclosed Switchgear

ANSI/IEEE C37.48-1992, Guide for Application, Operation and Maintenance of High-Voltage Fuses, Distribution Enclosed Single Pole Air Switches, Fuse Disconnecting Switches, and Accessories

NEMA ICS 3-1993, Factory Built Assemblies (including Part 2: Medium Voltage Controllers Rated 2001 to 7200 Volts AC)

UL 347 (1993), High-Voltage Industrial Control Equipment

2.3 Miscellaneous

ANSI/IEEE C37.100-1992, Standard Definitions for Power Switchgear

ANSI C84.1- 1995 Electric Power Systems and Equipment Voltage Ratings (60Hz)

NEMA ICS  1-1993  General Standard for Industrial Control & Systems

3. Definitions

The definitions contained in this standard are not intended to embrace all legitimate meanings of the terms. They are applicable only to the subject treated in this standard.

If a term is not defined in this standard, the definition in ANSI/IEEE C37.100 applies. The following definitions are not contained in, or differ from the definitions in, ANSI/IEEE C37.100.

3.1 blocking/rejection  interlock: A mechanical device which prevents the insertion of removable elements into a compartment with incompatible ratings or MOC operating capabilities

3.2 conversion: The process of altering existing power switchgear equipment from any qualified design.

3.3 design verification: The process of  design qualification, in accordance with all appropriate standards, of any conversion by means of design testing and/or evaluation, supported by justified technical evaluation and documentation.

3.4 modular assembly:

A circuit breaker element including interrupters, operating mechanism, and connecting terminals, or

an alternating current contactor element including interrupters, operating mechanism and connecting terminals, or

a molded case circuit breaker.

3.5 qualified design: Any power switchgear equipment which has been tested and certified to appropriate industry standards .

3.6 racking:: The act of moving a removable element physically between the connected position and the disconnected positions in its compartment

3.7 reconditioning: The process of maintaining existing power switchgear equipment in operating condition as recommended by the manufacturer’s instructions, using only the qualified design parts. Reverse engineered parts (designs copied from existing parts by other manufacturers) are not considered to be "qualified design parts" unless specifically design verified.

3.8 replacement interchangeable circuit breaker: A circuit breaker that that utilizes all new parts: has been designed tested  to ANSI/IEEE C37.09 or ANSI C37.50 as required; and requires no conversion of existing switchgear to maintain proper operation.

3.9 replacement non-interchangeable circuit breaker: A circuit breaker that utilizes all new parts and has been designed tested  to ANSI/IEEE C37.09 or ANSI C37.50 as required, but requires conversion of existing switchgear to maintain proper operation..

3.10 retrofill: A conversion process that includes replacement of the circuit breaker and circuit breaker compartment functional components of a  qualified design within a vertical section or compartment of a vertical section .with functional components of a different qualified design.

4. Service conditions

The service conditions specified in the standards listed in the references (see Clause 2)  apply to new equipment. Older equipment shall meet the service conditions in the standards that were in effect at the date of its manufacture unless the specified conversion process alters the equipment to meet the service conditions in the referenced standards. Any new and/or unusual service conditions shall be specified by the user.

5. Ratings

The ratings of new equipment are covered by the standards listed in References (Clause 2). The ratings of older equipment are covered by the standards that were in effect at the time of its manufacture. Converted equipment shall continue to meet the original ratings unless different ratings are specified and/or accepted by the user. All ratings shall be documented on the nameplate. Appropriate blocking/rejection interlock features are also required. When a circuit breaker is converted to a higher rating, the existing switchgear must also be evaluated for capability at this higher rating.

6. Conversion and testing

The conversion process can involve as little as a minor frame change to replacing main or arcing contact tips with other than the  qualified design material, or replacing the entire arc-interrupting structure and mechanism. This clause outlines known, specific examples of conversion, with the minimum testing required to verify the conversion. When multiple alterations are made, design tests may be combined for overall evaluation.

Design testing is required in accordance with the applicable standards listed in the References (Clause 2). Metal-enclosed devices shall be  tested in their applicable switchgear enclosures  as required by the referenced standards. Since alterations can affect the overall operation of the equipment, design verification of conversions is necessary.

All interlocking and mechanism operated cell (MOC) switch functions are critical to proper operation and shall be design verified in an  enclosure duplicating the intended installation. Additional design testing may be necessary when converted circuit breakers are required to be interchangeable with existing non-converted circuit breakers. Applicable portions of design tests can be utilized, with justified technical evaluation of the design alterations, to ensure that performance has not been adversely affected. Test data from previous similar qualified designs can be used for current designs, if clearly technically applicable.

Design verification data and the justified technical evaluation shall be available to the user, on request, to ensure that the converted equipment has been tested in accordance with this standard for continued service under installation conditions.

Any alterations to breaker or switchgear to accommodate a new trip device must not  violate NEC Article 240, paragraph 240-6(c) for "restricted access" when applicable.

6.1 Circuit Breakers and related conversions

6.1.1 Frames

Any alterations to the circuit breaker frame require design verification in accordance with ANSI C37.50 or ANSI/IEEE C37.09.

To ensure that all interlocking and auxiliary functions have been retained, racking tests shall be made in the original switchgear enclosure or in an enclosure duplicating the original in accordance with ANSI/IEEE C37.20.1 or ANSI/IEEE C37.20.2 for design verification. All metal-enclosed, dead-front features present in the qualified design, shall be retained.

6.1.2 Insulation structures

The insulation structure provided to support current-carrying parts or connecting bushings is specifically designed for mechanical strength as well as electrical and thermal life. Any alteration shall require design verification in accordance with ANSI C37.50 or ANSI/IEEE C37.09.

6.1.3 Contacts, supports, and primary disconnecting devices

Any alteration in the qualified design or manufacturing process of contacts, contact structures, contact supports, arc chutes or arc runners, or primary disconnecting devices, including material composition, brazing or plating, can affect overall performance and shall require design verification in accordance with ANSI C37.50 and ANSI/IEEE C37.20.1 or ANSI/IEEE C37.09 and ANSI/IEEE C37.20.2.

6.1.4 Medium- and high-voltage arc-interrupting structures

The arc-interrupting structures are designed to control and extinguish arcs. Conversion possibilities are given in the examples in 6.1.4.1 and 6.1.4.2.

6.1.4.1 Retaining the original structure (air-magnetic, air-blast, oil, etc.)

- Any original manufacturer’s recommended replacement parts or other qualified design replacement parts utilized  must  still be design verified.

- Air-magnetic circuit breaker arc-chute materials including splitter plates and liner plates are critical to proper operation and shall not be changed without a complete series of short-circuit current rating design tests in accordance with ANSI/IEEE  C37.09.

6.1.4.2 Conversion of the qualified  structure (air-magnetic, air-blast, oil, etc.)

When an interrupter conversion is made to a circuit breaker, there are several alternatives that vary in complexity as outlined in the following examples:

a) Conversions utilizing individual interrupters to replace only the interrupting structure and contacts require basic circuit breaker design changes such as the insulating structures for mounting and/or mechanism parts to modify stroke and force.

This type of conversion shall be subjected to the complete series of design tests in accordance with ANSI/IEEE C37.09 and ANSI/IEEE C37.20.2 to verify the circuit breaker for the ratings assigned.

b) Conversions utilizing a modular assembly,  may require alterations to the original circuit breaker frame to mount the modular assembly as well as to provide connections to the existing or new primary bushings, and may require revisions to insulation structures or components.

The modular assembly shall be subjected to the complete series of design tests in accordance with ANSI/IEEE C37.09. The design test data from the modular assembly tests may be utilized for design verification, if clearly applicable. Additional design tests shall be made on the complete conversion and shall include a dielectric withstand, momentary current, short-time current, continuous current, interlock, and other operational tests including tests to verify correct function with mechanism operated cell (MOC) switch assemblies, if applicable (see ANSI/IEEE C37.20.2 and sub-clause 6.1.7.2).

Mechanical endurance testing of the converted circuit breaker is required to at least the “between servicing” operational level requirements listed in ANSI C37.06. If the circuit breaker has no mechanism operated cell (MOC) switch operator, it may be tested separately but if a MOC switch operator is involved, it must be tested in the connected position in a duplicate of the switchgear vertical section to the same level.

In certain cases, the orientation and proximity of the bus connections between the modular units and the connection bushings can affect the short-circuit current capability of the sealed interrupters due to changes in magnetic fields around the interrupters. Sufficient short-circuit current testing shall be conducted for verification unless all configurations have been evaluated and documented by previous testing.

6.1.5 Low-voltage

Conversion of low-voltage power circuit breakers  may include the following types of alterations:

- Changing arc-interrupting structure (arc chutes) to eliminate asbestos

- Replacement of an earlier design circuit breaker with a  different design mounted on the same drawout structure

- Replacement of electro-mechanical or  electronic trip devices with a different electronic trip system

- Addition of fuses to an unfused circuit breaker

- Substitution of different current limiting fuses on a fused circuit breaker

- Replacement of arc interrupting structure with a  fused alternating current contactor element

6.1.5.1 Arc-interrupting structure

When ac or dc low-voltage circuit breaker arc chute designs are altered in any way, a complete series of short-circuit current and dielectric design tests shall be conducted in accordance with ANSI C37.50 for ac types and ANSI/IEEE C37.14 for dc types.

6.1.5.2 Circuit breaker substitution

When the existing circuit breaker is replaced with a different circuit breaker design utilizing the same circuit breaker frame structure, complete design tests shall be performed in accordance with ANSI C37.50 , ANSI/IEEE C37.14,  UL 489  and ANSI/IEEE C37.20.1.

6.1.5.3 Fuse addition or substitution

When fused low-voltage circuit breaker current limiting fuses are changed from the exact model and rating initially qualified in the configuration, design verification shall be required in accordance with ANSI C37.50. Dielectric withstand, continuous current, and short-circuit current tests shall be performed as appropriate to prove suitability of the application. It shall be verified by test that the maximum fuse let-through current does not exceed the capability of the circuit breaker without the fuse.  When current limiting fuses are added to an originally unfused circuit breaker, an open-fuse trip device is required. A series of the dielectric withstand, continuous current and short-circuit current tests is also required regardless of the fuse rating.  Dielectric testing is required to verify the ability of the fused conversion to satisfactorily withstand rated maximum voltage from either the line or load connections with blown, open or removed fuses. The test voltage shall be as specified by the appropriate apparatus standard.

6.1.5.4 Direct acting overcurrent trip devices

The conversion of low-voltage circuit breakers from electro-mechanical trip devices to electronic trip systems , or conversion of electronic trip systems  with different electronic trip systems, may require alteration of  the current-carrying structure, the sensor mounting, and the operating mechanism to adapt the new latch-tripping device, as well as the mechanical mounting of the electronic trip logic unit.

Design testing in accordance with ANSI C37.50 and ANSI C37.17 is required for each application of a trip system. All trip systems shall be installed and tested on the circuit breaker frame size for which they are intended to be applied. Upon successful design testing, production testing shall be performed in order to verify subsequent application.

6.1.6 Low-voltage and Medium-voltage operating mechanism parts and control wiring

When operating mechanism parts are replaced with other than the manufacturer’s recommended replacement parts, design verification is required in accordance with ANSI C37.50 or ANSI/IEEE C37.09.

Control wiring replacements shall be in compliance with ANSI/IEEE C37.20.1 or ANSI/IEEE C37.20.2. The replacement wiring shall be at least the same insulation temperature rating, ampacity, dielectric withstand capability, and flexibility as the original, or as required by the converted control system design. It is specifically noted that, for medium-voltage  conversions, the wiring shall be isolated from primary elements by grounded metal barriers with the exception of short lengths of wire at terminals, such as those of secondary disconnect devices or auxiliary switches, if provided on the  conversions.

Wiring changes shall undergo the necessary continuity checks and a dielectric withstand test in accordance with ANSI C37.50 and ANSI/IEEE C37.20.1, or ANSI/IEEE C37.09 and ANSI/IEEE C37.20.2 for design verification.

6.1.7 Low-voltage and Medium-voltage drawout parts, racking mechanisms, interlocking and other operational functions

Drawout interlocking and auxiliary functions as outlined in ANSI/IEEE C37.20.1 and ANSI/IEEE C37.20.2 are critical for the operation of the circuit breaker and shall be design verified [see item b) in 6.1.4.2.]

Testing, including mechanical endurance, shall be conducted in an  enclosure duplicating the intended installation. to insure the proper operation of all interlocking and other operational features.

If interchangeability with  existing circuit breakers is required, then additional alteration of existing vertical sections may be necessary and design verification  is required.  Mechanical and electrical interchangeability between converted circuit breakers and non-converted circuit breakers in a switchgear assembly may not be possible, for instance due to changes in control schemes. See 6.1.8 concerning requirements for warnings, instructions and blocking / rejection.

6.1.7.1 Racking Interlock functions

When the conversions require changes in the racking mechanism , design verification is required in accordance with ANSI/IEEE C37.20.1 or C37.20.2 as applicable. It is essential that the racking interlocking functions of the converted circuit breaker operate in an  enclosure duplicating the intended installation . For instance, racking interlocking for circuit breakers originally equipped with solenoid closing mechanisms shall be mechanically matched (electrical interlocking alone is not acceptable) with the new stored energy system to meet the requirements of ANSI/IEEE C37.20.2. During the racking procedure, the circuit breaker shall be open and closing shall be prevented unless the primary disconnecting devices are in full contact or are separated by a safe distance.

Regardless of the previous configuration of racking interlocks, all conversions shall be built in accordance with the  requirements previously outlined although modifications in the vertical section may be required for this capability.

6.1.7.2 MOC (mechanism-operated cell) switches or TOC (truck-operated cell) switches

If MOC (mechanism-operated cell) switches or TOC (truck-operated cell) switches  are mounted in the vertical section, whether altered or not, design verification of the assembly is required in accordance with ANSI/IEEE C37.20.1 or ANSI/IEEE C37.20.2, and item b) in 6.1.4.2.

A vital part of the conversion process is the coordination of the mechanism operated cell (MOC) switches with the converted circuit breaker to ensure proper operation. However, since the new, sealed interrupter, modular units may have much less mechanism power than the  circuit breakers they replace, they may not necessarily have sufficient reserve power to operate all installed MOC switches. This may necessitate substantial revision to or replacement of the MOC switches and their operating linkage in the existing vertical sections to assure proper operation. The converted circuit breaker shall satisfactorily operate with the maximum number of MOC switch contacts and spring return mechanisms that are recommended by the converter to be installed.

If MOC switch operation is limited, a prominent warning label shall be affixed to the circuit breaker indicating the limitation,  e.g., “This converted circuit breaker is not designed to operate a separate external auxiliary switch (MOC switch).” The instruction book and nameplate must also state limitations. The blocking/rejection interlock  shall be changed.

The MOC switch functionality shall be addressed as part of the conversion by both the converter and the user.

6.1.8 Control circuit coordination

The modular units used in conversions may have operators with different operating characteristics  than the original circuit breaker. These  differences  shall be taken into consideration, in cooperation with the user, to ensure total control and indication coordination and may require alteration or replacement of certain switchgear control circuit components.

The converter, in cooperation with the user  of the equipment to be converted, shall  determine any warnings, instructions and blocking/rejection that is needed for control circuit coordination at a particular installation. Instruction Books shall also provide these warnings.

.

Changes to the control circuit in a breaker compartment may be required when replacing a solenoid-operated breaker with a stored energy breaker. Modifications to the control schemes in the breaker compartment shall not result in an unintended closing operation of the previous design qualified device and shall be addressed during the design verification process.

6.1.9 Ground and Test Devices

6.1.9.1 Medium-Voltage Ground and Test Devices

Conversions of medium-voltage ground and test devices shall conform to all the requirements of ANSI/IEEE C37.20.6 and C37.20.2 to ensure that the devices have ratings and compartment capabilities no less than the circuit breaker they are intended to temporarily replace.

6.1.9.2 Low-Voltage Ground and Test Devices

Since no ANSI/IEEE Standard exists for these devices, they are custom devices confirming to manufacturer's design requirements and ratings.  They may be built in a configuration similar to those specified in C37.20.6, but the testing and application requirements shall be in accordance with the applicable requirements of C37.50 for Low-Voltage Power Circuit Breakers and C37.20.1 for Metal-Enclosed Low-Voltage Power Circuit-Breaker Switchgear.

The converter shall determine the ratings of the G&T Device to be converted from its nameplate, or if necessary, from the manufacturer.  The converted device shall have these same ratings unless increased ratings have been requested.  It must be recognized that the available short-circuit current rating of the device and its application cannot exceed the short-time rating of its compartment as specified in Table 2 of C37.16.  The ability of the device to close and carry its short-time rating for 0.5 second shall be demonstrated in a similar manner to the C-O portion of Test 8 in C37.50 Table 3.  If it is not possible to demonstrate an available peak current on closing as described in C37.50-3.9.3.3.3, it may be demonstrated in a separate test.  The ground connection system shall be tested in a similar manner to C37.20.6-7.3.2 except that the testing period is 0.5 second and the available short-circuit current cannot exceed the short-time rating of the switchgear ground bus.

The converter shall furnish a mechanical interlock bar on the G&T Device to prevent its inadvertent insertion into a circuit breaker compartment of the same frame size that has a higher available short-circuit current in accordance with Table 1 of C37.16.  The converter shall also modify or instruct the user on how to modify their compartments to allow the devices to be used in the proper compartments rated in accordance with their short-time ratings.  This will also distinguish the converted devices from new devices and compartments that may become available in the future that will be capable of meeting these higher ratings.

6.1.10 Alternating current drawout fused contactors

Conversions of both low-voltage and medium-voltage circuit breakers to alternating current fused contactors, utilizing modular  alternating current  contactor assemblies cannot be related directly to basic ANSI/IEEE standards as circuit breakers are. The only available standards that can apply in some manner are the NEMA ICS Series, UL347, and UL508. However, since alternating current fused contactor conversions do occur and since they are somewhat similar to low-voltage fused circuit breakers, the following clauses will provide guidance, using the fused low-voltage circuit breaker approach.  Dielectric testing is required to verify any fused conversion's ability to satisfactorily withstand rated maximum  voltage from either the line or load connections with blown, open or removed fuses. The test voltage level shall be as specified by the appropriate apparatus standard.

6.1.10.1 Frames. Alterations to basic circuit breaker frames shall be minimized and limited to those necessary to accommodate the qualified modular alternating current contactor, the current limiting fuse mountings, and the open fuse trip device for single phase protection adaptation.  All drawout features including interlocks shall be maintained.. A barrier shall be provided in front of and as part of the removable element to prevent access to primary energized parts when the compartment door is opened.

6.1.10.2 Insulation Structures. Alteration to the insulating structure of the circuit breaker shall be limited to assure continued dielectric  integrity. Medium-voltage alternating current fused contactors are not required to have an impulse withstand ( BIL) rating across the open contacts . Therefore, the insulation coordination of the total installation must be re-evaluated to assure compatibility with the  dielectric capabilities of the converted switchgear assembly. The exposure to over-voltages at the point of application in the distribution  system shall be evaluated, and action taken  to coordinate the insulation strength of the converted switchgear assembly with expected over-voltages, and to determine if supplemental surge-protective devices are necessary.

6.1.10.3 Current Carrying Parts. The basic current carrying parts, including the primary/secondary disconnecting devices of the circuit breaker may be modified to allow proper performance of the fused contactor and the other components in the switchgear.

6.1.10.4 Modular Assembly. The modular assembly shall be mounted within the basic circuit breaker frame with alterations kept to a minimum to maintain the mechanical and electrical integrity of the frame, the insulation structure and the current carrying parts.

6.1.10.5	Control Wiring.  The control wiring of the modular assembly, with the exception of the internal control wiring of the alternating current contactor, shall follow the requirements of clause 6.1.6.

6.1.10.6 Replacement Interchangeable or Non-interchangeable drawout assembly interlocking. The drawout parts/interlocking shall follow the circuit breaker conversion clauses (see clauses 6.1.7 and  6.1.7.1). MOC  switches, if used, shall receive specific design verification to prove reliability due to the lower actuation force of contactors,  Drawout mechanical interlocking is required to prevent racking of a closed contactor and to prevent its electrical or mechanical closing during racking. In addition, the contactor shall also be electrically interlocked to block a closing signal  during racking.. Blocking/rejection interlocking shall be provided on all contactor conversions to prevent insertion into a like circuit breaker compartment or into non-compatible contactor compartments.

6.1.10.7	Control Circuit Coordination. Control circuit coordination shall be in accordance with clause 6.1.8 including an evaluation of the control circuit power supply’s capability to operate the contactor conversion. within its operating limits. The coordination of protection shall also be reviewed. For instance, if the original protection scheme utilized an instantaneous trip function, it shall be defeated to prevent the possible errors in coordination  between the primary circuit fuse and the contactor during a short circuit interruption.

6.1.10.8 Testing. The NEMA Industrial Control Standards ICS-1, - 2 and -3 as well as UL 508 and UL 347 standards will provide some overall guidance. However, short-circuit current testing qualification for  low-voltage and medium-voltage alternating current fused contactors installed in metal-enclosed switchgear is not addressed in the existing standards.  The principles in ANSI C37.50 relating to testing of  low-voltage fused circuit breakers shall  be used as a guide in developing test requirements for low-voltage and medium voltage alternating current fused contactors. ANSI C37.50 specifically addresses the rated assigned maximum and cross-over short-circuit current levels to  ensure fuse protection of the modular unit at its maximum peak current withstand level. Appropriate use of all of these documents can provide for a design verified conversion with complete testing including continuous current, mechanical endurance, dielectric withstand and short-circuit current ratings. Dielectric testing is required to verify any fused conversion's ability of the fused conversion to satisfactorily withstand rated maximum voltage from either the line or load connections with blown, open or removed fuses. The test voltage shall be as specified by the appropriate apparatus standard.

6.2 Switchgear vertical sections

6.2.1 Vertical section

All design alterations to a switchgear vertical section require design verification. The following are examples:

a) Utilization of a non-interchangeable replacement circuit breakers or other conversions requires design alterations to fully coordinate with the vertical section interlocks and MOC and TOC switches. The resulting configuration shall be design verified.

b) Utilization of a circuit breaker completely tested to ANSI/IEEE C37.09, or to ANSI/IEEE C37.50 to replace another design of circuit breaker requires functional component replacement and design alterations to install the circuit breaker in the existing vertical section. The completed vertical section conversion shall be completely tested to ANSI/IEEE C37.20.2 or ANSI/IEEE C37.20.1 (as applicable)  . Examples of functional components include, but are not limited to: primary and secondary disconnecting devices, racking (drawout) mechanism, interlocks, and interconnecting buses .

c)When a complete, newly fabricated vertical section is constructed for expansion of the switchgear or as a replacement for a damaged section, any alteration from the original design shall require design verification. The design verification for these alterations shall be in accordance with ANSI/IEEE C37.20.1,  ANSI/IEEE C37.20.2., or ANSI/IEEE C37.20.3

d) Incorporation of a complete retrofill assembly of circuit breaker and compartment into an existing vertical section in place of the existing circuit breaker requires design verification of the new installation.

6.2.2 Bus, bus connections, bus supports and insulation

The switchgear bus, bus connections, current transformers, and insulation structure design are a balanced mechanical, electrical, and thermal system as initially designed.  If the switchgear assembly rating is to be increased for any reason, such as the installation of a converted circuit breaker of a higher rating,  technical evaluation and test of the assembly are required to  qualify  this increased rating. See ANSI/IEEE C37.20.1, ANSI/IEEE C37.20.2 or ANSI/IEEE C37.20.3.

6.2.3 Drawout parts/interlocking and other operational functions

These basic functions shall be retained in the converted equipment and any alterations to the existing or converted circuit breakers require design verification in accordance with ANSI/IEEE C37.20.1,  ANSI/IEEE C37.20.2, or ANSI/IEEE C37.20.3. When interchangeability between vertical sections is required,  modification/alignment of all circuit breaker interfaces shall be performed. Interchangeability is not always possible with existing, non-converted circuit breakers and may require changes in the blocking/rejection interlock features. Blocking/rejection interlocking shall be provided on all  conversions to prevent insertion of removable elements into non-compatible  compartments.

Any replacement of moving parts  with  other than the original design parts of the above equipment  requires design verification. This  may include mechanical endurance and other tests  in accordance with ANSI/IEEE C37.20.1,  ANSI/IEEE C37.20.2 or ANSI/IEEE C37.20.3.

If the primary disconnecting device design is altered, testing shall be correlated with the circuit breaker testing (see 6.1.3) in accordance with ANSI/IEEE C37.20.1 or ANSI/IEEE C37.20.2 for design verification.

6.2.4 Instrumentation and control devices & wiring

When current or voltage transformers, MOC or TOC switches, or similar components are replaced or additions are made, they should be a duplicate of the original design wherever practical. Replacement MOC or TOC switches shall have electrical ratings (interrupting, current carrying, and mechanical endurance) equal to or greater than those they replace unless lower capabilities are accepted by the user and qualified for the application. Replacement wiring, terminal blocks and terminal connections shall be as described in ANSI/IEEE C37.20.1, ANSI/IEEE C37.20.2, and ANSI/IEEE C37.20.3, and of at least the same ampacity, dielectric withstand capability, and flexibility as the original. For metal-clad switchgear, the control wiring shall be isolated from primary circuit elements by grounded metal barriers, with the exception of short lengths of wire at secondary disconnect and current transformer terminals.

Any replacement of moving parts by other than the qualified design parts of the above equipment will require mechanical endurance tests as well as continuity checks and dielectric withstand tests for design verification in accordance with ANSI/IEEE C37.20.1, ANSI/IEEE C37.20.2 and ANSI/IEEE C37.20.3.

6.3 Interrupter switchgear fuse conversions

Possible conversions of metal-enclosed interrupter switchgear include addition of fuses to equipment not originally designed to have power fuses, and substitution of power fuses of a different type or rating than the equipment was designed for.  Either type of conversion requires design verification.

- Conversion to add power fuses to metal-enclosed interrupter switchgear which was not designed with power fuses requires design verification in accordance with ANSI/IEEE C37.20.3 and ANSI C37.58.  If previous design test data is not available for the converted configuration, additional design tests shall be made on the complete conversion and shall include dielectric withstand, continuous current, short-circuit current-carrying, momentary current, and short-time current tests.  For current-limiting type power fuses, the short-circuit current tests shall be performed with designated power fuses with the maximum let-through current not exceeding the capability  of the switch.  For expulsion type power fuses, short-circuit current  tests to verify that the operation of the fuse in the enclosure does not adversely affect the mechanical and dielectric integrity of the enclosure  are required unless test data from previous tests on an equivalent configuration is  available.

- Addition of power fuses to equipment not designed to have power fuses requires the addition of interlocks to conform to ANSI/IEEE C37.20.3. These interlocks  prevent access to the power fuses unless the switch is open, and shall  prevent closing the switch when the power fuses are accessible.

- Conversion to substitute a different design of power fuses other than with which the equipment was designed,  requires design verification in accordance with ANSI/IEEE C37.20.3, and ANSI C37.58.  If previous design test data is not available for the converted configuration, additional design tests shall be made on the complete conversion and shall include dielectric withstand and short-circuit current tests.  For current-limiting type power fuses, the short-circuit current tests shall be performed with designated power fuses with the maximum let-through current for use with the switch.  For expulsion type power fuses, short-circuit current  tests to verify that the operation of the fuse in the enclosure does not adversely affect the mechanical and dielectric integrity of the enclosure  are required unless test data from previous tests on an equivalent configuration are available.

7. Production testing

Production testing of all conversions shall be in accordance with the applicable referenced standards ANSI C37.50 and ANSI/IEEE C37.20.1, or ANSI/IEEE C37.09 and ANSI/IEEE C37.20.2, or ANSI/IEEE C37.20.4 and  ANSI/IEEE C37.20.3,.

8. Nameplates

In order to ensure that the converted equipment performance ratings and responsibility for design are properly established, additional nameplates are necessary. Regardless of the complexity of the conversions, the original manufacturer’s nameplate shall be retained on the equipment for traceability (safety recall and/or renewal parts) and a conversion nameplate shall be added. The nameplate shall state the nature of the conversion and any limitations in interchangeability and ratings. The instruction book number will be stamped on the nameplate.

Each type of conversion shall be treated as follows:

·  For high-voltage circuit breakers or ground and test device conversions covered by 6.1.4.2 and 6.1.9, the original manufacturer’s ratings shall be marked “Converted” as shown in 8.1 or 8.2, if the ratings of the conversion are not changed.

·  For low-voltage circuit breaker conversions covered by 6.1.5, the original nameplate shall be marked “Converted” as shown in 8.1 or 8.2, if the ratings of the conversion are not changed.

·  For switchgear conversions covered by 6.2, the original nameplate remains valid with requirements in 8.3 also followed. Additionally, when only individual vertical sections are converted in any multiple switchgear lineup, the additional nameplate shall list the frame(s) that were converted, if the ratings of the conversion are not changed.

8.1 Individual interrupters

For conversions utilizing individual interrupters, such as in item a) in 6.1.4.2, a conversion nameplate shall be added near or adjacent to the original nameplate, including the words “Converted by” with the name of the organization performing the conversion, address, identification number, date, and all rating information in accordance with the nameplate requirements of ANSI/IEEE C37.04 and ANSI/IEEE C37.13, whichever is applicable.

8.2 Modular assemblies

For conversions utilizing modular assemblies, such as in item b) in 6.1.4.2, the additional conversion nameplate of the modular assembly manufacturer shall be provided on the unit, including the name, address, identification number, date, and all rating information, with an additional nameplate added to the circuit breaker near or adjacent to the original nameplate, including the words “Converted by” with the name of the organization performing the conversion, address, identification number, and date, in accordance with the requirements of ANSI/IEEE C37.13, ANSI/IEEE C37.14, or ANSI/IEEE C37.04.

8.3 Others

For all conversions, except as covered in 8.1 and 8.2, an additional conversion nameplate shall be added near or adjacent to the original nameplate, including the words “Converted by” with the name of the organization performing the conversion, address, identification number, new instruction book number, date, and nature of the conversion in accordance with the requirements of ANSI/IEEE C37.13, ANSI/IEEE C37.14, ANSI/IEEE C37.04, ANSI/IEEE C37.20.1, ANSI/IEEE C37.20.2 or  ANSI/IEEE C37.20.3.

9. Manuals

Installation, field test, maintenance, and renewal parts instruction manuals complete with drawings that cover the assembly/equipment installed or revised in the conversion process shall be provided. The manual shall include the expected electrical and mechanical interfaces between the converted circuit breaker and the compartment components including the component mounting inside the cubicle and the adjustments to ensure that they function together. This will include appropriate servicing and test methods and acceptance criteria of circuit breaker compartment mounted equipment such as interlocks and MOC switches to assure proper operation.

The converted  circuit breaker instruction manual shall state any limitations in MOC or TOC switches.

The instruction manual shall state whether the converted circuit breaker is or is not interchangeable with non-converted circuit breakers. Where converted circuit breakers are not interchangeable with non-converted circuit breakers, the instruction manual shall indicate interchangeability limits,

10. Recommended conversion design verification form.

The organization verifying that the conversion conforms to this standard shall:

a) Generate a complete tabulation of specific design qualification tests required by the C37 standards if this assembly after the conversion were a completely new design or developed circuit breaker or switchgear assembly as appropriate.

b) For each of these required tests, the specific test that was completed on the assembly after the conversion shall be identified or indication provided that the test was not required, with technical justification provided. The name, position, and responsible organization of the individual making this decision shall appear beside each line of the tabulation of tests with the approval date.

c) The conversion design verification form shall include the above information and identify the product as well as the engineering approval of the conformance. The document shall be issued as a controlled drawing and shall be permanently available for review upon request. The drawing number shall be included on the converter’s nameplate.

Annex A

(Informative)

Clarification of conversion processes

A.1 Introduction

This annex is provided for guidance in the design verification of the converted power switchgear equipment. It provides additional guidance regarding conversion examples and the minimum testing required for design verifications.

The owner of any power switchgear equipment to be converted shall plan and define responsibilities to assure that all components of the assembly are serviceable and coordinated, with particular emphasis on ratings, mating connections (such as those for primary current and secondary control), and all interlock functions and adjustments. In some cases such as replacing breakers with fused drawout contactors, the primary circuit protection schemes and dielectric withstand levels may require change.

It is important to recognize that production/field tests do not provide design verification. Design verification   can only be accomplished by design testing and technical evaluation.

A.2 Scope

This annex covers the power switchgear equipment conversions outlined in the basic standard. Clauses 1, 2, 3, 4, and 7 are sufficiently explained in the basic standard. However, Clause 6 has been expanded as a guide to ensure that conversions are design-verified as intended. Details included will be helpful regarding different conversion possibilities and in performing the test verification. However, the design tests specifically listed should not be interpreted to be the only tests necessary for the design verification.

A.3 Circuit Breakers

A.3.1 Frames (see 6.1.1)

The circuit breaker frame, if retained, should be carefully inspected. Some minor drilling and cutting is permissible, followed by repainting or plating as necessary. However, since other parts will probably be converted, the modified (converted) frame should be tested as part of the total conversion. Design testing shall include mechanical endurance tests to the “between servicing level” and momentary tests to ensure that the mechanical durability of the altered frame has not been reduced. Interlocking and auxiliary functions shall be proven by racking tests and mechanical endurance tests in a switchgear enclosure.

A.3.2 Insulation structure (see 6.1.2)

The insulation structure is critical and any change such as substitution of different materials or a different configuration requires material qualification for flame resistance and tracking, with design testing to include momentary, dielectric withstand, and mechanical endurance tests. It should be noted that insulation testing to determine long time endurance in practical field environments requires evaluation beyond simple dielectric withstand tests.

A.3.3 Contacts, supports, and primary disconnecting devices (see 6.1.3)

Any alteration in the original design of the contacts, contact structures, contact supports, primary disconnecting devices, or in material content or plating can affect overall performance and requires design verification. Design testing should include close-and-latch, short-circuit current interrupting, and mechanical endurance tests. A continuous-current test should be performed if the alteration modifies the current path, increases the electrical resistance of the current path (as compared to the original design value) or reduces the effective cooling airflow.

A.3.4 Medium- and high-voltage arc-interrupting structures (see 6.1.4)

This subclause is sufficiently outlined in the standard. However, it is stressed that conversion of arc-interrupting structures creates a new design and complete design testing is required.

A.3.5 Low-voltage arc interrupting structures (see 6.1.5.1)

This subclause is also sufficiently outlined in the standard. It is stressed that conversions of arc-interrupting structures create a new design and complete design testing is required.

A.3.6 Fuse replacement (see 6.1.5.3)

Replacing fused low-voltage power circuit breaker current-limiting fuses with a different design fuse, though mechanically the same dimensions, requires design testing. There may be mechanical blocking/rejection means, thermal, peak-current let-through, and crossover current differences. Design testing should be conducted to include, at the least, a continuous-current test and short-circuit current close-open interrupting tests at both the maximum short-circuit current rating of the fused circuit breaker and at the 635 V  short-circuit current rating of the unfused circuit breaker.

When adding current-limiting fuses to a previously unfused circuit breaker to increase its short-circuit current capability, the proper mechanical mounting needs to be developed with design verification of the mechanical alterations and to prove the dielectric withstand, continuous and short-circuit current capabilities, regardless of the fuse continuous current rating.

A.3.7 Direct-acting ac overcurrent trip devices (see 6.1.5.4)

Design verification is required in accordance with ANSI/IEEE C37.13 and ANSI C37.17 for basic design parameters, and ANSI C37.50 for basic test parameters. Each frame size converted circuit breaker, unfused or fused, shall be design tested in accordance with the concepts in 3.9.4.3 and 3.9.4.4 of ANSI C37.50, but at both the minimum and maximum sensor ratings at the energy input level corresponding to the actual system voltage on which the converted circuit breaker is applied. The corresponding short-circuit current is listed in ANSI C37.16 for that voltage. For fused circuit breakers, this is in addition to the testing required in 6.1.5.3.

All electronic direct acting overcurrent trip systems used shall be adapted, mounted, and design tested on the circuit breaker. Production tests shall be carried out on each converted breaker.

Some low voltage circuit breakers tripping devices take advantage of a making release device, therefore meeting the requirements of ANSI C37.50 paragraph 3.5.9 "except when equipped with instantaneous tripping elements during closing". When installing new trip devices, which are not equipped with a making current release, the converter must conduct short-time current tests in accordance with ANSI C37.50. It should not be assumed that all circuit breakers have been tested to the short-time duty cycle specified by ANSI C37.50.

A.3.8 Low and medium- voltage fused ac contactors

When circuit breakers are converted using modular ac contactors, they must always be fused to meet or exceed the short-circuit current capability of the metal enclosed switchgear in which they will be used.  An unfused contactor does not have the current withstand capabilities of a circuit breaker, and thus always needs current limiting fuses added to provide protection for maximum short-circuit levels and overload currents exceeding the capability of the unfused contactor itself.  Since contactors do not have the full capabilities of a circuit breaker, contactor conversions must be technically evaluated and design-verified (including testing) to assure the proper rating and application for each particular power switchgear equipment conversion application.

While design and production testing of fused alternating current contactor conversions is not covered in the referenced standards, it is possible to apply some of the fused circuit breaker testing principles outlined in ANSI C37.50.  These basic principles are valid for both low-voltage and medium-voltage contactor conversions.

The endurance ratings of modular unfused ac contactors vary widely among manufacturers, and it is impractical to perform endurance (open / close) tests to the ultimate capability of the contactor.  However, the converter should perform mechanical (no-load, open / close) tests of the complete conversion in the switchgear cell, to the requirements of the relevant standards.  For medium-voltage contactor conversions, the test should conform to UL 347 clause 27 (6000 operations).  For low-voltage contactor conversions, the test should conform to UL 508, clause 43, with the exception that the tests should be conducted as no-load operations and the minimum number of operations should be 6000.  For either medium-voltage or low-voltage, “operation” means one complete sequence of a close action followed by an open action.

A.3.9 Addition to or change in power fusing of switches used in metal-enclosed switchgear

Metal-enclosed interrupter switchgear generally utilizes the load-break interrupter type switches, which may be unfused or fused, with either the expulsion or current-limiting type of power fuse.  After installation and years of service, circumstances may require some conversion due to available short-circuit current increase or for changed protection needs of individual circuits

Any conversion of a qualified design unfused switch to a fused configuration requires many design changes and design verification.  The converter must consider the short-circuit current rating of the converted design, the continuous current temperature limits, dielectric requirements, enclosure mechanical strength, and the like.  The conversion must also consider the short-circuit current withstand capability of the basic unfused switch, to be sure the current level prior to fuse interruption will not damage the switch.

There are three basic types of conversion of fused switches to use a different size or type of fuse other than in the original qualified design.  Conversion to a smaller fuse of the same type and model requires no design verification other than that related to mechanical fit.  Conversion to larger fuse of the same type and model requires verification of short-circuit withstand, continuous current temperature rise, dielectric capability, and enclosure integrity.  Conversion to a fuse of a different type or model requires verification of short-circuit current withstand, continuous current temperature rise, dielectric capability, and enclosure integrity.    The user must also recognize that substitution of expulsion fuses in place of current-limiting fuses may have system protection implications, since the expulsion fuse does not have a current-limiting characteristic. Replacing an expulsion fuse with a current limiting fuse may have system surge protection implications due to associated voltage transients and may require arrestors with a higher MCOV if this is consistent with dielectric coordination of system insulation components.

A.3.10 Mechanism parts and control wiring (see 6.1.6)

When mechanism parts are replaced with parts different in material, material hardness, or bearing design, for example, a mechanical endurance test must be conducted. Closing and tripping speeds and forces can also be affected and should be checked.

A.3.11 Low-voltage and Medium-voltage drawout parts, racking mechanisms, interlocking and other operational functions (see 6.1.7)

When worn or broken parts are replaced with parts different in material, material hardness, or bearing design, design testing shall be conducted. A major alteration to the drawout system could affect the hold-in capability of the circuit breaker under maximum short-circuit current conditions and should be tested.

When the conversions covered in item b) in 6.1.4.2 are made and redesign of the interlocking is necessary, design testing shall be conducted in an enclosure to ensure interchangeability of the converted circuit breaker in its own vertical section, as well as in other sections as necessary (see 6.1.7.1).

Operating functions for mechanism-operated cell switches (MOC) or truck-operated cell (TOC) switches shall be provided. The 6.1.4.2 a) conversions generally utilize existing functions. However, for 6.1.4.2 b) conversions, it may be necessary to increase the number of auxiliary switches and/or the means to operate the existing MOC switch. This would require changes to the blocking/rejection interlocks and also design verification (see 6.1.7.2).

# A3.12 Control Circuit Coordination (see 6.1.8)

There may also be control schematic or operating characteristic changes during the conversion process that result in incompatibility of the converted product with the non-converted configuration. ANSI/IEEE C37.20.1 and C37.20.2 do not require blocking for various types of control schemes. If the conversion implementation process results in both converted and non-converted switchgear to be located at or available to the same facility, special attention by the user and converter may be necessary to avoid hazardous operating conditions

If required, a label shall be installed on the circuit breaker and the compartment, to warn of control circuit coordination. The Instruction Books shall also warn of this characteristic.

A typical example might be as follows:

Warning - the controls circuits on this device may not fully function in all compartments. It is essential that complete compatibility be established prior to inserting this breaker into an energized primary circuit.

A.4 Switchgear vertical sections

A.4.1 Basic vertical section (see 6.2.1)

The basic vertical section, if retained, should not have the materials and weldments changed. Some minor drilling and cutting is permissible, followed by repainting as necessary. However, any major alteration should be tested as part of the total conversion with design testing coordinated with the circuit breaker changes. Testing shall include mechanical endurance, short time, and momentary tests to ensure suitability of the altered section. This should include the circuit breaker hold-in mechanism if altered. Interlocking and auxiliary functions should be proven by the racking tests.

If the design of the primary disconnect is altered, testing should be correlated with the circuit breaker testing in A.3.3.

A.4.2 Bus, bus connections, and insulation (see 6.2.2)

The switchgear bus, bus connections, and insulation structure design are a balanced mechanical, electrical, and thermal system, and any replacements that are not of the same design and materials, including the bus-joint covers, may require design testing.

When a complete, newly fabricated vertical section is constructed for expansion of switchgear or as a replacement for a damaged section, any alteration from the original design, including secondary disconnects, shall be design tested.  Depending on the alterations made, the design testing conducted should include the following: insulation material properties; mechanical drawout functions and alignment; momentary current; continuous current; and dielectric withstand capability.

If the design of the primary disconnect device is altered, or the basic circuit breaker rating is increased, dielectric withstand, momentary current withstand, short-time current withstand, and possibly continuous-current tests shall be made in a switchgear enclosure.

A.4.3 Low-voltage and Medium-voltage drawout parts, racking mechanisms, interlocking and other operational functions  (see 6.2.3)

These basic functions shall be retained and matched to the existing or converted circuit breaker with interchangeability and design testing conducted.

A.5 Additional MOC switch design verification

The design of a MOC switch for use with an air-magnetic or oil circuit breaker may require much more energy to drive it than the MOC switch for a modern sealed interrupter circuit breaker.  The operating mechanism of a sealed interrupter design may not have sufficient reserve power to meet its close and latch rating while operating the maximum number of MOC switch contacts that may be installed in the switchgear vertical section.  The highest energy requirement, normally occurring during a circuit breaker closing operation, may result in a stalled circuit breaker mechanism or intermittent contact making when closed on a high fault.

Design Verification:

- The maximum energy required for closing shall be determined by the converter with an adequate and stated margin to allow for practical field conditions when the lubrication may not be ideal. The justification for the adequacy of margin shall be stated.

- The MOC switch assumed shall be stated with clear limitations of the number of contacts and the service condition of the complete assembly. If blocking/rejection interlock modifications are required to limit application (e.g., to restrict the number of MOC switch contacts or energy required), the revised blocking/rejection interlocks shall be provided.

- Travel curves for both opening and closing shall be taken which show velocity, timing, rebound, and bounce within accepted limits as defined and proven by power testing for the assembly.

- No load endurance testing to at least the “between servicing” intervals shown in ANSI C37.06 or ANSI C37.16 shall be conducted with no mechanical deterioration of any of the parts of the assembly which would prevent the breaker assembly from immediately performing its rated duty cycle.

- Minimum short-circuit testing shall include closing on maximum asymmetrical short circuit current in accordance with the requirements of ANSI C37.50 or ANSI/IEEE C37.09, and shall include a successful opening operation after a cooling period following a full rating closing operation.

A. 6 Typical information to be documented for a conversion

Specific Information of Conversion from Converter:

# Technical Authority for all aspects of Conversion

Name:

Address:	Street:

City: 				  State: 		  Zip:

Contact:	Name: 				  Phone:

Fax: 				  E-Mail:

Design Verification Drawing Number: _______________Rev #______ Date_______________

Note:	Certified test data and Design Verification   to be available from above Technical Authority.

## Specific Intent of Conversion:

Completed Conversion Ratings:

Current Rating: Continuous ____ A, Interrupting ____ kA, Close & Latch ____ kA

Voltage Rating ____ V, Current Ratings:  Continuous ____A

Short Circuit ____kA

Close & Latch ____kA

units of current to be stated i.e.. rms amps, peak amps

Arc Chute Replacement:  Manufacturer 			  Part Number______________

Fuse Replacement or Addition

Manufacturer: 				  Type: 			  CAT # 		  Voltage ____ V,  Continuous Current 	_A, Interrupting Rating 		kA

Trip Unit Replacement

Manufacturer of Conversion Kit

Type 					  Model

Power Supply:   N/A, Internal ____ V   ac   dc, External ____ V   ac   dc

Interrupter Replacement

Interrupter Manufacturer

Model 					  Part Number

Fuses Required:    Yes   No  See above for fuses installed.

Interrupter Replacement with Modular Assembly

Modular Unit Manufacturer

Model 					  Part Number 						
		Voltage Rating ____ V, Frequency:   60 Hz.   50 Hz.

Trip Coil:  Manufacturer_________ Part Number: _____________ Volts ____   ac   dc

Close Coil: Manufacturer: ________ Part Number: _________ Volts    ac   dc

Charging Motor: Mfgr.: __________ Part Number: _______ Volts ____   ac   dc 			Latching Mechanism:   YES    NO, Aux. Contacts on circuit breaker : ____ a, ____b

Wiring Diag. Number

Trip Functions:	  LT    ST    INST.     G,  CT or Sensor Rating

Switchgear Modification Required:    YES   NO,

Other Breaker Modifications: List Separately

Switchgear

Replace or Upgrade Bus:  Material:   Al    Cu, Voltage Rating: ____ V

Current Rating:  Continuous: ____A,  Short Circuit: ____ kA , momentary__________kA

Insulation Material

Racking Mechanism Modifications:

Describe: ______________________________________

MOC Replacement:  Manufacturer: ______ Part No. _______

Contacts: ___ a, ___ b 	 Note each cell must be specified

TOC Replacement:   Manufacturer: _______ Part No. _______ Contacts: ___ a, ___ b

Barrier Modifications:  Describe

Insulation Modifications:  Describe

Typical Information to be provided by Customer/User to the converter:

Name:

Address:  Street 				 City: 		_______	State:  _____ Zip

Contact:   Name:  _______________________________ Phone:

Fax:  _________________________________ E-Mail:

Date of Information_________________

# Original Equipment Information … Provided by Customer,  … Obtained by Converter Inspection

Circuit Breaker

Manufacturer:  			 Type:  		  Model:  	__  Voltage: 	V

Continuous Current:  ____ A,  Short Circuit Rating: ____ kA, ____mVA

Control Voltage:  Trip _____   AC    DC    N/A,  Close_____     AC    DC     N/A

Number Aux contacts wired out from breaker		a		b

Shunt Trip:    Yes    No,  Undervoltage Trip:    Yes    No

LV Trip Unit

Manufacturer:  			Type:  				  Model:

Trip Functions:    LT    ST    I    G,     CT or Sensor Rating:

Fuse

Manufacturer:  				Type:  		  Cat #:  _______________

Voltage:  _____ V,  Continuous Current:  _____ A,  Interrupting Rating:  _____ kA

Switchgear

Manufacture:  __________________________ Type:  		_  Model:

Voltage:  _____ V, Main Bus Rating:  _____ A, Short Circuit Rating:  _____ kA

Number Compartment Contacts:  … N/A,    MOC: ___a ___b

TOC:  ___ a, ___b

Modification To Be Performed:

LV Circuit Breaker

…	Arc Chute Replacement

- Main or arcing contact replacement

…	Trip Unit Replacement:  Preferred Manufacturer:_____________________ Model: ___________

Cat. No.:  ______________ Trip Elements:  …LT  … ST  … I  … G

…	Change Air Magnetic Contacts to Sealed Interrupter:

Load Characteristics:  … Motor:  IFL ____  A, ILR _____ A ,   … Fixed:  _____ A,  … Other:  Describe

Open Fuse Trip Device:    Yes    No,  Shunt Trip:    Yes    No, Latched Interrupter:    Yes    No

Switchgear Modification Required:	 Yes    No  … Converter to Determine

MV Breaker

Arc Chute Replacement

Bushing Replacement

Interphase Barrier Replacement

Trip Coil Replacement

Close Coil Replacement

Charging Motor Replacement

…	Change Air Magnetic Contacts to Sealed Interrupter:

Load Characteristics:  … Motor:  IFL ____  A, ILR _____ A ,   … Fixed:  _____ A,

… Other:  Describe________________________________________________________

____________________________________________________________________________

Switchgear Modification Required:  Yes    No  … Converter to Determine

Switchgear

… Bus Modification: … Rating, … Insulation, …  Supports, … Other Components

…  Convert compartment or section for new type breaker

…  Modify or Change MOC and/or TOC

…  Control wiring changes

…  Convert Section for Retrofill

… PT or CPT switch changes