F02HVCBa6 - HVCB First-pole-to-clear Task Force

The HVCB First-pole-to-clear Task Force met on Tuesday Oct. 1, 2002 with 26 present, of which 6 were members.  Ken Edwards presented graphs displaying the differences of the TRV ratings from the IEEE 1979, IEEE 1999, IEC 2000, and proposed harmonization standards.  Discussion ensued around the test duty T60 where the harmonized value was below both the IEEE 1999 and IEC 2000 standards.  The task force concluded that the issue should be addressed in the HVCB TRV Revision WG.  Kirk Smith agreed to provide IEC studies that were used to develop the harmonization rating to those attending.  In addition seven utility representatives agreed to provide system configurations to compare with the studies to establish validity for use in North America.

Rod Sauls presented survey results of a survey conducted by Tom Fields relating to the need for a first-pole-to-clear factor of 1.5.  It was agreed that if a survey is considered it should be written and conducted by the task force to avoid biases.

John Brunke presented calculations of system first-pole-to-clear requirements for Bonneville Power Administration.  Discussion resulted in the need for users to determine the system needs for the appropriate first-pole-to-clear factor.  Seven utility representatives agreed to conduct calculations of required first-pole-to-clear factor for their respective systems.  These requirements are to be discussed at the next meeting. The meeting was adjourned with the above action items.

Ken Edwards

High Voltage Equipment Services

Bonneville Power Administration

TNSD/PPO2-2

PO Box 61409

Vancouver, WA 98666-1409

Ph. (360) 619-6093

Fax (360) 619-6946

Cell (360) 607-0483