Working Group PC37. 06 Revision of

“AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis – Preferred Ratings and Related Required Capabilities”.

24 September 2003, from 8:00 AM to 12:00 PM

17 members 15 guests participated to the meeting.

- As the PAR to include C37.06.1 in C37.06 failed, it was decided to include the revised pages of C37.06.1 in PC37.06.

- Discussion and general comments were based on draft 3B.

- Comments from Chuck Wagner, Yasin Musa, Denis Dufournet, and Devki Sharma were discussed.

- Some philosophical concept discussed as commented by Chuck Wagner from the Blue Book.

- We were not able to have the same values than the IEC standards due to different concepts and historical raisons..

- Corrections will be added with the new tables due to early errors.

- Some key subjects that were discussed:

- Tables to be coordinated with C37.016 - Circuit Switchers.

- IEC Coordination of prospective transient recovery voltage for T10 that list a RRRV of 7 kV/µs is OK for the RRRV but not for the peak values.

- New tables for recovery voltages were proposed based on the conclusions the working group C37.04.

- Capacitance applications: Roy Alexander working group 09a and with inclusion of the C0, C1 and C2 concepts inside C37.06.

- To take care of the line fault, John Brunke will perform some test in BPA in late September. Based upon the results, we will have to include the Line Fault (LF) might be included to take into account mutual coupling between lines.(90 miles to 8 miles)

- No change of voltages will be included in this document today, based on the preliminary proposal of Tom Tobin to the IEC of coordination of medium voltages between IEC and IEEE.

- Assigned: The verification of the values of the Tables was assigned to 24 persons distributed in 6 working groups to check all the values of all the tables. (About 250 calculations for each working group). Each working group is made of 50% of users and 50% of manufacturers.

- Thank you for the efforts to all the participants of these working groups.

- The intention is to ballot C37.06-200x with the C37.04, 09 & 011.