MEETING AGENDA:

PLACE:			Portland, OR

| GROUP | DATES of MEETINGS | TIME of MEETINGS |
| --- | --- | --- |
| IEEE TRV Working Group | Monday Oct 22, 2003 | 10:15 AM to 3:15 PM |

| Item | Agenda Item Description | Person |
| --- | --- | --- |
| 1. | WELCOME | Kirk Smith |
| 2. | # Review of Decisions from Spring Meeting | Kirk Smith |
| 3 | # Summary of Changes in PC37.04-200x Draft 05 | Kirk Smith |
| 4 | # Review of Complilation of Comments to Draft 04 | Kirk Smith |
|  | # and |  |
| 5 | # Review of PC37.04-200x Draft 05 | Kirk Smith |
| 6 | # Assignment of tasks as required | Kirk Smith |
| 7 | SET TIME AND PLACE FOR NEXT MEETING | Kirk Smith |

| 2. | # Review of Decisions from Spring Meeting | Kirk Smith |
| --- | --- | --- |

The decisions made in the May 2003 were reviewed. These are found in document TRV Working Group May 2003.doc attached to these minutes.

| 3 | # Summary of Changes in PC37.04-200x Draft 05 | Kirk Smith |
| --- | --- | --- |

- TRV Multipliers

General 	- Same as IEEE C37.06

Specific 	- t2(@T60) = 0.5 x t2(@T100)

Others	- not for RRRVs at 100 kV and Above

The result of the change in the t2 multiplier at T60 to 0.5 is illustrated in the attached figure 4 from C37.04-200X - D05 showing the family of TRVs from T10 through T100.

Figure 4A family of 4-parameter TRV Envelopes typical of TRVs for ratings 100kV and above

- RRRVs

| ### Test Duty | RRRV in kV / sec |
| --- | --- |
| T100 | 2 |
| T60 | 3 |
| T30 | 5 |
| T10 | 7 |

RRRV at T10 is changed back to 7 kV / sec instead of RRRV beieng a variable with voltage. Subsequent to the May 2003 meeting, the IEC maintenance team MT34 for IEC 62271-100 decided that the variable RRRVs did not make sense since they did not allow the use of convenient multipiers. Therefore, the 7 kV / usec value for a rated voltages from 100 kV and above will be re-instated.

- Kpp

- Less than 100 kV		Kpp = 1.5

Many systems ungrounded

Both 3-phase grounded and 3-phase ungrounded faults need Kpp = 1.5

- 100 kV and above		both Kpp = 1.3 and Kpp = 1.5 available, user chooses

Most systems grounded

3-phase ungrounded faults represent < 1% of faults observed

Kpp = 1.3	covers most cases

Kpp = 1.5 available for impedance grounded systems

Kpp = 1.5 available

for cases where 3-phase ungrounded faults are more common

or

where users want the extra capability

- Kaf

Kaf = 1.4 as decided last meeting

- Appendix explaning OP Values

An edited version of write-up on TRV for Out-of-phase by Eiichi Haginomori dated 2000-Sept-27 provided for TRV revision of IEC 62271-100

- T10 & T30 2-parameter TRVs – why is td = 0.15 x t3 ??

TRVs at T100 and T60 were ex-cos envelopes in previous IEEE standards

- 4 parameter reference lines plus delay line is equivalent description

- td	=	2 sec is arbitrary choice made by both IEC and IEEE circa 1990

- represents delay of exponential part of TRV caused by small bus capacitance

TRVs at T10 and T30 were 1-cosines in previous IEEE standards

2-parameter reference lines plus delay line is equivalent description

Uc	=	E2

t3	=	0.88 x T2

since reference line of TRV is tangent to 1-cosine from above

td	=	0.15 x t3

since delay line of TRV is tangent to 1-cosine from below

| 4 | # Review of Complilation of Comments to Draft 04 | Kirk Smith |
| --- | --- | --- |
|  | # and |  |
| 5 | # Review of PC37.04-200x Draft 05 | Kirk Smith |

The complilation or comments on Draft 4 was reviewed. See the attached document for details. The chairman’s responses to the comments were incorporated into Draft 5.

Highlights of draft 5 were reviewed.

PLAN:

- The chair will re-send out Draft 5 (with a few obvious fixes), the compilation of comments to Draft 4 and a blank comment form with a request for comments to be returned by the end of October.

- Chair to prepare draft 6 and send out by the end of December 2003.

ACTION ITEMS for WORKING GROUP MEMBERS:

- Prepare comments on draft 5 and return to the chairman by the end of October.