C37.09a Capacitance Current Switching

Meeting in Portland OR  9/23/03

Notes of interest

The meeting was attended by 9 members and 20 guests.

Draft 10 was successfully recirculated with only 2 negatives.  As recirculated, draft 10 has a very open definition for class C0,  allowing an unlimited number of restrikes, which literally allows multiple restrikes on each operation.

As background, it was clarified that each capacitance current switching duty, to which a rating is assigned, will have a corresponding probability of restrike assigned.

The only mandatory capacitance current switching duties are:  overhead line switching for outdoor breakers, and cable switching for indoor breakers.  All other ratings are at the option of the user.

After considerable discussion it was agreed that the requirements for passing C0 classification shall be one (1) restrike per operation.

It was also agreed that class C0 will be available for circuit breakers rated 72.5kV and below.

Action items:

- Recirculate a D11 with requirements for passing C0 as one restrike per operation.

- Consult Yvette Hosang on the best way to get C3704a revised to include Class     C0.

- Request a PAR to revise/replace C37.04a

- Upon PAR approval, immediately ballot the addition of class C0 to C37.04a.

The meeting was adjourned.

Grace & Peace

Roy Alexander

Chair WG on Capacitance Current Switching C37.04a and C37.09a.