From: Pete Dwyer [petedwyer@Intergate.com]

Sent: Wednesday, October 05, 2005 12:45 PM

To: Bill Long; Bergman, Bill; Ward E Laubach; Ted Olsen; Ted Burse;

Sullivan, Paul B; Puckett, Robert J; Dwyer, Pete W.; Pat DiLillo; Nigel

P McQuin; Mike Orosz; Lester, George N; Gray, Keith; Gill, Harpinder S;

Doug Edwards; Barnhart, Paul; Albert. Livshitz

Subject: Minutes of C37.59 w/g Meeting October 4th, 2005

Minutes of C37.59 w/g Meeting October 4th, 2005			05 October 05

The working group met at 2PM with 9 members and a total of 22 persons present

in Montreal. After the initial introductions and review of the patent policy slide, D4

was discussed which had been circulated in September.

The agenda was to review D4 and to modify it as agreed by the majority.

These modifications would be incorporated then a balloting pool would be

requested coincident with a request for IEEE editing review.

After much discussion and a vote, it was decided to move the details under

6.1.5.4 back from the annex to the body of the standard.

There was also technical concern about the interlocking of two sets of

racking assembled and electrical connections in some versions of modular

drawout assemblies. In these conversions a new breaker with its primary &

secondary disconnects and drawout system is mounted on an existing drawout

frame. An expanded interlock requirement is to be drafted by Albert

Livshitz.

Nigel McQuin indicated that his editorial suggestions had been missed in the

generation of D4.

Ted Olsen also documented a number of editorial changes and provided a mark

up to the Chair.

The chair will make the recommended changes and initiate the balloting

process as planned so that we may have results before the next meeting.

Pete Dwyer   w/g chair Rev of C37.59 Conversions of Switchgear