Reclosers and Other Distribution Equipment (RODE) Subcommittee

Meeting Minutes

Milwaukee, Wisconsin – October 3, 2006

| Members | Present: | Guests: |
| --- | --- | --- |
| Jerry Baskin Ray Capra Marcel Fortin Harry Hirz George House Ed Jankowich Don Martin Steve Meiners | Don Parker Tim Royster Francois Soulard Ken Workman Jan Zawadzki Ed Steel Dave Stone | Antone Bonner Frank DeCesaro Walt Von Miller Nenad Uzelec Thomas Tobin Gerard Schoonenberg Peter Glaesman Tim Fink |

1.   CALL TO ORDER

Chairman Steve Meiners called the meeting to order at 2:00 PM.   There were 15 members and 8 guests present. The current RODE membership is 28 (see attached membership roster).

2.   INTRODUCTIONS

Members and guests introduced themselves.

IEEE Patent By-laws clause 6 & inappropriate topics were presented to the subcommittee.

3.   MEMBERSHIP CHANGES

Jim Swank is a new member.

4.   APPROVAL OF MINUTES

The Spring 2006 meeting minutes were approved without change.

5.   CHAIRMAN’S REPORT

ADSCOM’s meeting summary was reported.  See ADSCOM meeting minutes.

Chris Ambrose has accepted the position as RODE Vice Chair/Secretary.

6.  WORKING GROUP REPORTS

a) Recloser Standard C37.60  This is a possible new working group.  Working Group Chairmen are Bob Behl and Dave Stone, and Bob Behl reported the following:

The Study Group for the revision of C37.60-2003 held its third meeting on October 4, 2006 in Milwaukee, WI.  Twenty-three persons were in attendance.  See attachment 1 for the attendance list.

(Note: Until the PAR is submitted and approved by IEEE, there cannot be an official Working Group)

The IEEE policy for patents and guidelines for the conduct of meetings (inappropriate topics of discussion) were reviewed.

IEEE C37.60-2003 is an IEEE/IEC Dual Logo standard.  Thus the project work will include the input solicited from IEC and an effort to have the new revised standard re-approved by IEC to retain its international standard status.  Mr. M. Ceglia indicated that the process would start when the PAR is approved.  IEEE will then notify IEC and ask if they wish to participate.

Co-Chair Behl reported on the progress of the PAR.  It has been drafted and will be finalized and submitted to IEEE before the October 19 deadline for the December RevCom meeting.

Co-Chair Stone gave a brief review of the history of the “recloser” standard.  See attachment 2.

Twenty-four individuals have indicated an interest in becoming members of the Working Group.  This is a large group and while no person will be refused for WG membership, Co-Chair Stone asked that all of these prospective members consider the expectations of the Chairpersons.  These expectations were outlined as:

Key word is “engagement”

- Attend Working Group meetings if possible; although this is not mandatory

- Accept assignments

- Respond to correspondence

- Provide feed-back

The Chairpersons will contact each person who indicated interest in becoming a member of the WG by e-mail after the PAR has been approved by RevCom and ask them to re-affirm that interest by return e-mail.  Those that respond in the affirmative will be added to the WG list.

Discussion of the revision activity anticipated for the standard included the following topics:

- IEC Dual Logo Considerations; noted above

- Input from the Task Force Solid Dielectrics Task Force (Chaired by Chris Ambrose)

The work of the Task Force may not be complete in time to be included in this revision.

- Input from the Task Force Controls (Chaired by Don Parker)

The Task Force is moving toward requesting a PAR; no report has been issued as yet.  The work of the Task Force or a subsequent WG may not be complete in time to be included in this revision.

- Adoption of C37.100.1 – Common Requirements

This is anticipated to be a large portion of the WG’s activity.  Several persons present volunteered to review parts of C37.100.1 to access its potential for use with C37.60.  The Chairpersons will develop a format or guide to assist in this review and distribute to the volunteers with specific assignments to be established.

- Partial Discharge test limits.  Chairpersons will contact members present representing several manufacturers and users to solicit experience with partial discharge testing.  Messrs. M. Fortin, F. Soulard, ???, and D. Stone will prepare a questionnaire for this purpose.  Results of this survey will be used by the WG to determine if the partial discharge testing section should be revised or expanded.

- Other revision to be defined.  D. Stone will research the records from the previous WG activities to see if any items were deferred and should be taken up now.  All members present were asked to submit items, questions, or ideas for improving the standard to the Chairpersons.

The meeting adjourned at 12:00 noon.

Attachment 1: Attendance List:

| Name | Company |
| --- | --- |
| Aberg, Kris | Northeast Utilities |
| Baskin, Jerry | Federal Pacific |
| Behl, Bob | ABB |
| Capra, Raymond L. | Consultant |
| Culhane, Michael | Cooper Power Systems |
| Fortin, Marcel | Consultant: Electrical T& D |
| Glaesman, Peter | Reuel, Inc |
| Hirz, Harry | Joslyn Hi-Voltage |
| Jankowich, Edward M. | Thomas & Betts |
| Martin, Donald R. | G & W Electric Co |
| Meiners, Steve | General Electric |
| Myers, Tim | Cooper Power Systems |
| Pinsky, Alla | Cooper Power Systems |
| Ross, Charles | FKI Switchgear |
| Royster, Timothy E. | Dominion Virginia Power |
| Schoonenberg, Gerard | Eaton Holec |
| Soulard, Francois | Hydro-Qurebec |
| Steele, Ed | Joslyn Hi-Voltage Corp |
| Stone, David T. | DTS Technical Services |
| Swank, Jim | Cooper Power Systems |
| Uzelac, Nenad | G&W |
| von Miller, Walt | Reuel, Inc |
| Workman, Ken | Schweitzer Engineering Inc |

Background of IEEE C37.60

- USAS C37.60-1968

  - Took the automatic recloser portion out of C37.22-1959

  - Left the sectionalizer portion behind

- ANSI/IEEE C37.60-1974

  - Revised section 5.3 Interruption

  - Revised section 7.3 Position Indicator

  - Tables 2 & 3 (ratings)

- ANSI/IEEE C37.60-1981  (Reaffirmed in 1988)

  - Expanded to include padmount and submersible reclosers

  - Added information for vacuum interrupters

  - New and expanded info on test requirements, particularly switching tests

  - Added surge withstand capability requirements

  - Expanded production test requirements

  - Included “recognition of the need for partial discharge tests for some type of reclosers.”  However the procedure and related requirements were not finalized.

- IEEE C37.60-2003

  - a) Expanded standard to include gas-insulated reclosers.

  - b) Limited scope to 38 kV

  - c) Added voltage ratings commonly used outside of North America

  - d) Added new interrupting ratings

  - e) Revised limits of temperature and temperature rise 	consistent with circuit breaker standards.

  - f) Referenced IEEE Std 1247-1998 for switching test procedures.

  - g) Removed requirement for transf. magnetizing tests

  - h) Removed the altitude correction factors.

  - i) Added transient recovery voltage (TRV) specs

  - j) Restricted the use of single-phase testing to verify three-phase performance.

  - k) Reduced radio influence voltage (RIV) limits.

  - l) Added Partial Discharge as a design and production test.

  - m) Reduced dc withstand voltage test time to 5 min.

  - n) Achieved IEC Dual Logo Status

b) Capacitor Switch Standard C37.66  Working Group Chairman Harry Hirz reported the following:

Standard is now published and available for purchase, date March 2006.

c) Underground Switchgear Standard C37.74  Working Group Chairman Steve Meiners reported the following:

Open meeting with welcome and introductions.  A roster sheet was circulated and a request to identify on the sign-in sheet desire to be a member of this working group.

IEEE patent clause 6 & inappropriate topics were presented to those present.

There were 19 individuals in attendance, and 11 have volunteered to be members of this working group.  Membership will remain open for this team, for some individuals were not in attendance for this meeting.

The current state of this standard is a publication of 2003 and is time for us to begin working on a revision.

Motion made for acceptance of the meeting minutes from May 2006.  Minutes were attached to the RODE subcommittee minutes.  No objection to those meetings and the motion to accept was carried.

Request was made for everyone to use an IEEE alias e-mail address if you do not have one to go create it.  Very easy to create from Myballott go to My Profile and there you can enter the address id you chose and where you want the e-mail to be forwarded to.

- Reviewed comments submitted by Ed Jankowich.

| Page | Section | Paragraph | Existing | Proposed |
| --- | --- | --- | --- | --- |
| iv | Introduction | 7 | None. | Suggest adding a comment about the purpose of IEEE Std 1247 relative to this document that we are reviewing. |
| 3 | 3 | --- | New entry requested | Suggest adding a definition for a “fused way”. This term is used repeatedly throughout this document. |
| 5 | 5, Title | --- | Ratings, required related capabilities, and test requirements | I have described the use of these terms to other people without much success. There is little recognition from people outside of our working group about the distinction to be made in these three categories. If nothing else we should provide a definition of them. I also suggest when we use the terms in our document, we preserve the order of the second term. We sometimes refer to it as “related required capabilities”. |
| 5 | 5.2.1 | --- | Table 2. | Suggest revising this listing to include other ratings established in Table 2. |
| 13 | 6.1.4 | 1st | Frequency of the supply voltage. | This document calls out a tolerance of 10% while IEEE Std 1247, Section 8.3.1.5 calls out a tolerance of 2%. This should be resolved in this revision. |
| 17 | 6.6.2 | 1st | Test Sequence is not defined. | I was looking for parallels between Section 6.4.2, 6.5.2 and 6.6.2. In the first two sections we defined the test sequence, but not in the 3rd section. |

| 18 | 6.7.1 | 1st | Last sentence. | Suggest deleting since the new revision of IEEE Std 1247 was published, presumably with the corrections. |
| --- | --- | --- | --- | --- |
| 18 | 6.7.1 | 1st | Entire sentence. | This sentence seems to contradict the intent described in Section 6, 2nd paragraph, first sentence. |
| 18 | 6.7.1 | 3rd | Figure 2. | Suggest adding a footnote to indicate that Line nos. 4 – 9 are only done when there is a common insulating media between phases. |
| 20 | 6.7.2 | 2nd | a | Since we are referencing IEEE Std 4, why not use the established tolerances for defining the impulse waveshape? |
| 22 | 6.7.4.1 | 2nd and 3rd | Entire content. | These two paragraphs describe a very common condition that can exist with laboratory equipment. But, what is the designer expected to do to resolve the dilemma? |
| 23 | 6.7.4.2 | 1st | Last sentence. | If these tests are meant to demonstrate mechanical integrity as well as electrical capability, shouldn’t these tests be performed at the rated maximum voltages shown in Table 1? |
| 24 | 6.7.4.3 | 2nd | First Sentence. | See comment to 6.7.4.2. |
| 27 | 6.7.5.4 | Table 8 | 2nd column. | Why aren’t fused loadbreak ways included in this table? |
| 27 | 6.7.5.4 | Note | Existing. | Suggest deleting since the new revision of IEEE Std 1247 was published, presumably with the corrections. |

| 28 | 6.7.5.6 | Note | Existing. | Suggest deleting since the new revision of IEEE Std 1247 was published, presumably with the corrections. |
| --- | --- | --- | --- | --- |
| 31 | 7.4 | 1st | Gauge pressure. | Why is this requirement greater than the design requirement in Section 6.7.9.2? |
| 33 | 9 | All | Entire section. | Recommend this section be harmonized with IEEE Std C37.60 since both DSG are used in the same environments. |
| 34 | 9.10 | 1st | 2nd sentence. | I am not certain what is being suggested in the second sentence. |
| 38 | Annex A | Table A.1 | 4th main column | Unless I am mistaken, rms factors are a ratio of two currents and should have them shown in parenthesis as done in the previous column. |

Discussed paragraph 6.7.4.5.2 on Automatic Fault interrupters used as switches and it was agreed that clarification is needed here.

Also, it was agreed that harmonizing with C37.100.1 will be undertaken in this WG.

Several references are made to 1247 in the standard and this will be reviewed for further references and adequacy of those already made.

A PAR has been submitted and a copy of the submitted request was presented.  Revision will be by NesCom admin once the revised wording is agreed upon.  Review of the revised wording is being conducted with Ted Olsen.  It is expected that approval for the revised wording and approval of the PAR during December NesCom meeting.

These standards to be used as reference have been circulated.

- C37.74-2003

- IEEE 386 (ballot copy)

- C57.12.28-1999, also C57.12.29

- IEEE 1247 (C37.39)

For comments we will use the existing method of putting comments into the comment from and sending to WG Chair for correlation prior to our next meeting.

It was discussed in the meeting that the WG members would return completed comment forms to Steve Meiners before end of year.  They will be correlated into a document and reviewed during our next meeting.

Chuck Ball presented a proposal for a change in NEC Article 490 to add Service Entrance requirements to Padmount switches.  These construction features, if adopted, would involve many changes to the current standard design switch.  Attached to this report are copies of the NEC proposal on this change as well as the forms to complete to request disapproval of this proposal.  The forms will be attached in Word format to the e-mail distribution list.

Opportunity was given at this time for any additional comments and/or questions.  None were voiced and a motion to adjourn was made and seconded.

d) Task Force on Controls for Distribution Equipment   Task Force Chairman Don Parker:

- Call meeting to order.

Don Parker was introduced as the new chairperson of the taskforce.  Frank DeCesaro, the acting chairperson, will assist with meeting notes.

The IEEE-SA Standards Board Bylaws on Patents in Standards and Inappropriate Topics for IEEE WG Meetings slides were displayed to the group and discussed.

Each of the (16) participants introduced themselves.

- Minutes of last meeting – Corrections, approval

The minutes of the May 8, 2006 meeting were displayed on screen and approved with no additions or changes.

- Review status of previous assignments

ENVIRONMENTAL: Chuck Ball stated that draft of section 5 was created about a year ago and should be found in the other minutes.

The May 8, 2006 meeting minutes reported that defining whether ambient temperature for controls should be obtained outside or inside of the control cabinet had yet to be resolved. Chuck’s initial thought was to have this defined outside of the control cabinet since it would cover varying conditions between different pieces of equipment such as different solar loading additions or affects of nearby equipment.   This is supported by the definitions of IEEE C37.100.  Questions arise whether this then applies to controls located inside equipment cabinets or outside. Since temperatures within equipment cabinets can attain higher temperatures than the defined external ambient, would not it be appropriate to have terminology or nameplate data maximum working temperature of the air space where the control resides in?  Don Parker noted that temperatures driven by solar gain have caused problems for his company.  Further discussion pointed out that low or high temperatures could cause battery and processor problems.  There could be a 15 to 20 degree difference between outside ambient and the air space within equipment based on radiated solar energy.  Should this guide suggest this more as a required statement?  The guide can expand to defer to the manufacturer for inside temperature concerns.

A question was raised whether controls are tested inside or outside of switchgear.  The response indicated that controls are normally tested to their rated extremes using environmental chambers.  One manufacturer stated that once the control leaves the factory the user could throw a lot of equipment in the chamber with heat producing equipment unknown to the manufacturer. That is why it is important to have manufacturers specify the maximum temperature controls should reside in.  Chuck Ball’s group will add these concerns to his group’s recommendation.

A comment was made that the group should also deal with the functionality of equipment during the test.  Is equipment to be rejected if the LCD display malfunctions at  –30 C or –40 C but the rest of the equipment functions properly? Should 100% of the equipment  be expected to be functional or is it ok to have items such as an LCD go out?

If the users test their equipment for frost or humidity, should the control access doors be closed or open?  Do manufacturer test for both conditions?  Chuck commented that frost was one of the things his group wanted to include but has not been able to find papers other than one Bill Hurst originally provided. The easy approach is to say that the control should be able to withstand conditions inside the equipment that it is to be utilized. If its door is opened under frost or humidity then it should be tested that way. The guide is to supplement users.  It is not a standard.  If a guide becomes a standard, then the working group assigned will deal with this.  A question was raised whether extended events such as ice storms are a problem?  One manufacturer stated not in their experience.  The control is located inside the enclosure and any condensation is on colder part, which is on the outside of the padmount, not in the control cabinet inside the padmount.  This guide should deal with nominal conditions. It was suggested that we consider that  events such as an extended ice storm are unusual conditions where other standards refer the user to the manufacturer.

ACTION ITEM: Don requested Chuck’s group to produce an updated draft of the section that we can all view later. Chuck stated that there are two cases, one for control in a specific device made for that device and can be tested as a whole.  Then a control that anyone can buy and use.  He thinks we may possibly recommend conditions around the control, not around the switchgear within which  it is located. Chuck will forward the draft to the taskforce before the next meeting for comments.

ACTION ITEM: Frank is to provide email addresses to Chuck.

MECHANICAL:  Bill Hurst has been the leader of the mechanical group.  There are still questions remaining from the last meeting.  These were:

- What if the mechanical vibration was seismic?  One utility is dealing with pole vibration from this.

- Bob Behl had explained about a MEOST (sp??) test his company is performing which follows a guide on DOT testing for vibration.  Bob was to forward that to Frank for sharing with the taskforce.  He had mentioned a seminar in Florida he wanted to attend and then share information.

Since Bill Hurst had changed jobs, he will not be able to actively participate in this taskforce.  Ed Steele volunteered to lead this.  Jerry Baskin agreed to work with Ed.  Post Meeting Note: Frank talked with Bill Hurst and he confirmed that he would not be able to actively participate in the meetings.  He wants to remain as a corresponding member of the taskforce.

ACTION ITEM: Frank will look through his hard copy information and pass whatever he finds relating on this group to Ed.

ACTION ITEM: Francois Soulard will send Ed an email with a list of standards that Hydro Quebec has.

HARMONICS:  John Angelis is the lead person of this group.  Post Meeting Note: Don Parker contacted John after the meeting and was informed that John would like to be replaced a the group leader.  He will remain as a corresponding member.

ACTION ITEM:  We need a volunteer from the taskforce to lead this section.  Please contact Don Parker at DMPARKER@southernco.com before the next meeting if you feel you can help the taskforce out in this area.

From the last meeting:

- Ken Workman will send a list of standards that SEL uses to John.  Update - Ken had not been able to forward the standards by this meeting but will.

- Francois Soulard reported that he just received authorization to proceed with function and interference tests on controls.  Controls will be installed on a real time simulator at Ireq(sp?).  He will try to provide feedback on their findings.  Update – Francois reported that these tests are now scheduled for the end of October.  He will report the results to the group.

Grounding Variations: Harry Hirz is the lead person for this group.  Ken Workman reported that they had some discussions between meetings.  There is a large amount of informal work available but nothing adequately covering this. Grounding variations are different around the world and specifications are normally up to the local utility.  Once installed, grounds are normally not checked.

Hydro Quebec (HQ) uses 120 V transformer that are six poles away at times and controls can fail as a result of this design.  A comment was made that manufacturer recommendations deviate from the reality.  HQ wants this aspect raised, particularly regarding grounding.  At HQ, any pole with equipment gets a ground rod installed.  Variability of ground is a concern.  The control is affected when it is at the bottom of a pole and there is a lack of ground.  HQ checks ground continuity once a year.  About 1% of equipment experiences ground problems.  Remember that environment conditions affect the ground resistance.  There can be from 25  to 2000 variation.  HQ checks whether the grounds are open.  They are not concerned about one rod in practice.  They check the entire grid configuration.  Francois stated that IREQ worked on analyzing ground grids on distribution systems and predicted problems in the future.  In the past the presence of  a metallic water pipe connected to a water heater  improved the grounding. However now  the use of  plastic water pipes are now causing changes in the ground resistance.  They have to check grounding more often in neighborhoods.  Switching surges and surge arrester operation affect voltage bounce.  Controls and equipment grounds are tied together.  It was commented that there has been 15 V between neutral and ground need to be maintained.  He feels UL and CSA agree.  A comment was made that OSHA talks about grounding grids and voltage during faults.   If a rod is installed and 25  is not maintained then an additional two rods are installed and you are done.  The utility does not check back to see if you have the 25 . This group should research reports on utility standards or guidelines for information on grounding techniques and accepted values.

Some utilities only drive a rod and do not check for impedance.  They hope it is ok.

Don Parker stated that a meter commonly used to measure ground resistance will obtain only the 60 Hz impedance for installed grounds.  He recalls reading that a manufacturer was proposing equipment to look at grounding impedance’s at higher frequencies.  Lightning manifests itself in the 1 MHz range.  There are differentials between recloser and control grounds.  The grounding wire configuration used is also a factor.

HQ recommends a straight line from recloser to control, no bends allowed.

Don Parker suggests that this team give consideration to a section addressing the 60 Hz grounding and an additional section that addresses lightning frequency grounding and include a summary of how the two are different.

EMI: Bob Behl is the leader of this group.  He is at the October meetings but not able to attend our session.

ACTION ITEM: Frank will email MIL 461E to the group.  This standard is in the public domain.  He will also contact Bob to obtain a syllabus on a course Bob was taking regarding EMI.

Lightning and other surges: Frank DeCesaro is the leader of this group.  There were no action items for this meeting other than providing a summary.  This was not worked on between meetings.  Ed Steele and Nenand Uzelac will also join this group.

Functional requirements: It was decided that another group was needed.  Francois Soulard will lead it.   Ken Workman will also help.

It was commented that the ANSI C37.11 philosophy should be considered. Section 3 deals with functional requirements and Section 4 is on devices and auxiliaries.  Although this refers to breakers, the principles and ideas behind it are very basic to us.  The committee should look at this standard and sort what is applicable to our group.  It was suggested by Steve Meiners that this taskforce needs to watch scope creep.  It appears that we are getting broad in our mission.  The group may want to refine what is meant by functional requirements. The group needs to deal with basic functions such as the state of equipment and priority of operations.  As an example, a breaker that is in its closed state should remain closed if a control is connected to it.  There are instances that the equipment changes to match the state of the control being connected.  That should not happen.  Francois stated that the logic behind a function not provide specifics such as speed, etc.  Functional requirements should deal with the safety purposes.  Ex relays define 52A and 52B contacts.

ACTION ITEM: Don Parker should obtain a copy of this ANSI C37.11 for use by the taskforce.

User/Manufacturer Survey: Francois Soulard is the leader of this group. We have had difficulty getting a survey out since the beginning of this taskforce.  A survey was accepted last time.  It has been distributed in Canada with zero response.

Francois suggests that we go distribute the survey through the Internet. He will investigate how.  Francois suggested that members of this taskforce not answer the survey since we are all very active.  We should get others in our companies to complete it.

Francois discussed HQ’s testing specification and that he compiled the different standards they use.  This was provided to Frank who will email to the group.

Ed Steele commented that there is a web site called undergroundnetworks.com.  It is similar to an open chat room but deals with utility problems and gets quick responses back. This site deals with more than just underground networks.  They address transformers, etc.

ACTION ITEM: Don Parker will determine if this survey can be distributed to switchgear committee.  We should also contact the relay committee to get assistance in the survey. Manufacturer members of the task force should inquire if their companies have access to an on-line survey site that could be used.  If so, contact Francois.

- Miscellaneous action items for next meeting

Frank will look at any hard copy paperwork dealing with this taskforce and create a PDF to email it to members.

Ed Jankowich has many IEC documents that could be useful to the group.  We need to get a final determination if any IEC documents we need have to be sourced from the IEEE or does our right to them allow a member to share theirs?  Post meeting note: Frank checked with Matt Ceglia of the IEEE and was told that members will be violating copyright law if they supply IEC documents to the taskforce.  Any copyrighted standard needs to come from the IEEE.

- PAR Wording

Steve Meiners asked if the taskforce felt it has enough background to go to the next level and submit a PAR to create a guide?  Don Parker felt there was as did the concensus of the attendees.  The following suggested PAR was developed.

SCOPE:

This guide presents the basic considerations for application of distribution equipment controls with equipment rated above 1000 V and up to 38 kV on overhead and underground electrical distribution systems.  This guide includes considerations and various tests for:

Environmental factors
	Mechanical vibration
	Harmonics
	Grounding
	Electromagnetic interference
	Functional requirements
	Lightning and switching surges

PURPOSE:

This guide presents the basic considerations for application of distribution equipment controls with equipment rated above 1000 V and up to 38 kV on overhead and underground electrical distribution systems.  This guide includes considerations and various tests for:

Environmental factors
	Mechanical vibration
	Harmonics
	Grounding
	Electromagnetic interference
	Functional requirements
	Lightning and switching surges

ACTION: Don Parker will discuss the PAR statement with Ted Olsen, Jodie Haasz, Matt Ceglia, and Jeff Nelson on the wording between this meeting and next.  Any required modifications can be made between meetings via email with the task force.

- These meeting minutes were prepared and respectfully submitted by Frank DeCesaro.

e) Task Force on Solid Dielectric  Equipment   Task Force Chairman Chris Ambrose (excused) Bob Behl & Marcel Fortin chaired this session and reported the following:

Chair: Bob Behl filling in for Chris Ambrose

Vice-Chair / Secretary: Marcel Fortin

Introduction and Roster

The task force meeting convened at 1:30 PM.  Fifteen people signed the Task Force Roster sheet.  The Roster is attached.

IEEE Slides on Patents and Inappropriate Topics

The required slides on patents and the need to avoid commercial issues were presented.  No concerns were raised on these issues.

Task Force Theme

Do the existing standards adequately cover the design and testing for the solid dielectric equipment?

Many manufacturers are producing solid dielectric equipment, and the users are concerned that this is not properly addressed by the existing standards.

The manufacturers and testing facilities should be able today specify the thermal cycle tests and other tests that are needed for solid dielectric equipment.

That way we could very soon be able to add these necessary requirements to the standard which would greatly benefit the industry.

Discussions

- Need to get input from Cigre has a WG in solid dielectric, WG A3.21, “Aspects for the application of non-ceramic insulators to HV and MV apparatus”

- Bob Behl gave presentation on Thermal Cycling of Hydro Phobic Cycloaliphatic Epoxy (HCEP).  The highlight of this discussion was that finding flaws in the HCEP material appears to be only related to taking the solid dielectric assembly down to -60C.  Secondly, the findings were that heat and ramp rate did not affect the results.  Will provide more detail in Spring Meeting.

- Gerard Schonenberg gave a presentation on IEC 62271-201.  This standard is the High Voltage Switchgear and Control Gear Part 201: AC insulation-enclosed switchgear & controlgear for rated voltages above 1kV and up to and including 52kV.  The highlight of this discussion was the Annex D – insulation protection grades and testing requirements.

- Don Parker insists that many cycles are needed to find flaws in solid dielectric material.

- Several comments were made to the effect that the thermal cycling procedure will be different for different materials.

- Flaws found after thermal cycling may not necessarily be found by partial discharge tests.  Sometimes only Hi-Pot testing will uncover flaws.

User Expectations (Important - carryover from Galveston meeting)

- New equipment - we want to make sure that they will last for 40 to 50 years in service.

- Similar materials are out on the system for many years now. Expected life for utilities is 40 to 50 years. What do we want and what do we expect.

- The depreciation life is 30, but we expect more.

- The expectation is no end of life. We don’t know these polymers will perform. Whole different sort of materials that perform and react differently.

- Expect 40 years for all type of materials.

- Rapid temperature aging simulates aging.

- Curing and changes with time. And curing with time. Surface reactions.

- Emphasize the complexity of aging (chemical, mechanical interfaces, surfaces exposure to chemical and electric field). Literature search is necessary.

- Optical instrument experience. Emphasize the importance of thermal cycling. 3 out of 6 units failed. 35 thermal cycles

- Manufacturer change the insulator shape, the skirt was not good for insulation contamination. Changing from porcelain to polymer is not straightforward. The washability of the material and UV or chemical changes.

- Look at insulator standards for aging tests, tracking wheel, etc.

- Cigre: effect of the insulation system on the interrupter and vice versa.

- Several types of solid insulation material

- Summary of the tests performed by HQ. Lineman’s perception is that the surface gets bad looking with time. Some equipment is followed for 7 years.

- Are the actual interrupters tested at extreme temperature specified in the standard?   Manufacturer Yes.

Manufacturing realities (Carry over from Galveston)

- IEEE 386.  Is this applicable to solid dielectric equipment?  Is it enough?

- Some do thermal cycle test; do they add on or not. Can we induce failures or failure modes that would never occur in the field?

- Might these tests be prematurely aging the materials and inducing additional defects?

- What is the field experience? Is there a problem out there? Products are good out of the box but how will they perform down the road.

- Be very specific in defining the thermal cycle. Does the interior achieve the desired temperature? How long to keep it at -40 to make sure the interior gets to the assigned temperature.  What rate of rise?

- The environment and application parameters have a major impact on the life. Different material will have different behavior (i.e. glass transition temperatures).

Action items and assignments - (some items continued from Galveston Meeting)

- All - Send the chair a list of all the applicable standards and/or papers that can be relevant. This was partially complete but needs work.

- Chris, Bob Behl, and Marcel Fortin will complete the bibliography search.

- All - rank the papers

- Chris will get the papers and assign readers.

- Readers report to the TF at the Spring meeting.

- Bob Behl to get permission to circulate IEC 60298 and 60466.

- Bob Behl to identify important areas in IEC standards.

7.   OLD BUSINESS

None.

8.   NEW BUSINESS

NEC proposed change, Article 490, to include Service Entrance requirements and specific construction features on incoming switches – could impact Padmount switch assemblies if accepted.

9. NEXT MEETINGS:

- 6-10 May 2007, St. Pete Beach,

- 30 Sept - 4 Oct 2007, Pittsburg, PA. or Philadelphia, PA

- 4-8 May 2008, Portland, OR or Las Vegas, NV

Respectively yours,

Steven Meiners

Chairman

RODE Subcommittee

Attachments:

See S06RODEa1 - RODE Standards Status Report.

See S06RODEa2 - RODE Membership Roster