Reclosers and Other Distribution Equipment (RODE) Subcommittee

Meeting Minutes

St. Pete Beach, Florida – May 8, 2007

| Members | Present: | Guests: |
| --- | --- | --- |
| Jerry Baskin Ray Capra Marcel Fortin Harry Hirz George House Ed Jankowich Don Martin Steve Meiners Bob Behl Chris Ambrose | Don Parker Tim Royster Francois Soulard Ken Workman Jan Zawadzki Bill Walter Dave Stone John Wood Jim Swank | Larry Davis Frank DeCesaro Walt Von Miller Nenad Uzelec Thomas Tobin Craig Befus Peter Glaesman Tim Fink Sebastien Riopel Mark Stavnes Glenn Borchard Jeff Gieger Michael LaBianco Fernando Ciprian |

1.   CALL TO ORDER

Chairman Steve Meiners called the meeting to order at 2:00 PM.   There were 20 members and 14 guests present. The current RODE membership is 28 (see attached membership roster).

2.   INTRODUCTIONS

Members and guests introduced themselves.

IEEE Patent By-laws clause 6 & inappropriate topics were presented to the subcommittee.

3.   MEMBERSHIP CHANGES

No membership changes.

4.   APPROVAL OF MINUTES

The Fall 2006 meeting minutes were approved without change.

5.   CHAIRMAN’S REPORT

ADSCOM’s meeting summary was reported.  See ADSCOM meeting minutes.

6.  WORKING GROUP REPORTS

a) Recloser Standard C37.60  This is a new working group.  Working Group Chairmen are Bob Behl and Dave Stone, and Bob Behl reported the following:

The Working Group for the revision of C37.60-2003 held its fourth meeting on the afternoon of May 8, 2007 in St. Pete Beach, FL.

The agenda was reviewed followed by introductions.  Thirty-four persons were in attendance, twenty five of whom signed up as WG members.  See Annex A for the attendance list.

The new 5-slide (5/1/2007) IEEE policy for patents and guidelines for the conduct of meetings (inappropriate topics of discussion) was reviewed.

Background of C37.60

The background of the standard was reviewed as follows:

- USAS C37.60-1968

- ANSI/IEEE C37.60-1974

- ANSI/IEEE C37.60-1981

- (Reaffirmed in 1988)

- IEEE C37.60-2003

  - a) Add gas-insulated reclosers.

  - b) Added IEC voltage ratings and new inter ratings

  - c) Revised limits of temperature and temperature rise consistent with circuit breaker standards.

  - d) Removed req’t for transf. magnetizing tests

  - e) Removed the altitude correction factors.

  - f) Added transient recovery voltage (TRV) specs

  - g) Restricted the use of single-phase testing to verify three-phase performance.

  - h) Reduced radio influence voltage (RIV) limits.

  - i) Added Partial Discharge as a design and production test.

  - j) Reduced dc withstand voltage test time to 5 min.

  - k)   Achieved IEC Dual Logo Status - 2005

PAR Status

The PAR was approved in December 2006 with Dave Stone and Bob Behl as Chair and Co-Chairpersons respectively.  The PAR also recognizes that this is an IEC/IEEE Dual Logo standard.

Dual Logo Status

Chairman Stone gave a brief update of the status of the dual logo.  The standard was approved by IEC in September of 2005 by a slim margin and designated at IEC 62271-111.  Comments submitted with the ballot included:

- FDIS ballot that did not allow National Committee a chance to change the standard..

- Lack of definitions in the standard for terms not defined in the IEC [IEV] dictionary.

- Format, including clause numbering does not follow IEC practice

- IEC Common Specifications 60694 is not references

- Normative References do not include IEC documents.

At the IEC SC17A plenary meeting in Delhi, India on April 17, 2007, the Sub-Committee voted to support the Dual Logo Maintenance Team (DLMT) in the revision of the standard.  The IEC National Committees have until the end of June to appoint experts to serve on the DLMT.  These experts will become members of the IEEE/IEC Joint Working Group and invited to attend future WG meetings.  David Stone has been nominated by the USNC to be the Convenor of the IEC MT47.

Details of the DLMT and Joint WG procedures are being reviewed by IEEE Staff.  Matt Ceglia will assist the WG as the details are worked out.

WG Membership

Chairman Stone reported that the formation of the official working group had been deferred until the PAR was approved.  Now that the PAR is approved, the group was invited to sign up as a WG member.  Twenty-five persons signed up at the meeting.  The WG membership is open to all IEEE members; others are expected to join in the weeks ahead.

Expectations of the WG were outlined with the key word being “engagement”.

Members are expected to:

- Attend Working Group meetings if possible

  - Not mandatory

  - Some meetings in conjunction with IEEE Switchgear meetings

  - Some meetings at other times, possibly in other countries depending upon the participation from IEC members of the Joint WG.

- Accept assignments

- Respond to correspondence

- Provide feed-back

WG Tasks/Assignments:

While the formation of the DLMT/Joint WG is complete, some work items were discussed and assignments made to volunteers.

- Compare IEEE/IEC Common Requirements documents (D. Stone and L. Farr).  One objective is to see if both documents can be used as parallel normative references.

- Re-organize numbering of C37.60 into IEC format. (D. Stone and L. Farr).  IEEE has approved this move; it will then match the numbering of IEEE C37.100,1 and IEC 62271-1, the respective common requirements documents.  See Annex B, a chart comparing the clause numbering (organization) of IEEE and IEC standards.

- Compare C37.60 and Common Requirements (Ed Jankwich).   Dave will send a copy of the renumbered C37.60 as soon as it is complete.  This exercise will identify which parts of C37.100.1 can be adopted “as is”, “with additions or exceptions”, or not at all.

- Compare normative references for parity (F. DeCesaro).  Objective is to see if any of the IEEE normative references have equivalents in IEC that can be used as parallel references.

- Identify definitions to bring into document  (Chris Ambrose and Bob Behl).  IEEE has indicated that it may allow definitions into the Definitions clause even if they are in IEEE 100 Dictionary.  This is important for IEC understanding.

Other items were suggested for consideration for general revision including the corrigendum, table on temperature rise, Annex A and B from the withdrawn application guide C37.61.

The meeting adjourned at 5:30 PM.

Annex A: Attendance and Preliminary WG List:

IEEE C37.60 Working Group Meeting May 8, 2007

| Name | Company Affiliation | WG Member | Attended May 2007 Mtg |
| --- | --- | --- | --- |
| Ambrose, Chris | Florida Power & Light (DEO-PDC) | Yes | Yes |
| Bannink, Harm | KEMA-Powertest, Inc. |  | Yes |
| Baskin, Jerry | Federal Pacific | Yes | Yes |
| Befus, Craig | BC Hydro | Yes | Yes |
| Behl, Bob | ABB | Yes | Yes |
| Borchardt, Glenn | S&C electric Co | Yes | Yes |
| Capra, Raymond L. | Consultant | Yes | Yes |
| Davis, Larry | Reuel, Inc | Yes | Yes |
| DeCesaro, Frank | Cooper Power Systems | Yes | Yes |
| Dotson, Randall | Lakeland Electric | Yes | Yes |
| Falkingham, Leslie | VIL | Yes | Yes |
| Farr, Larry | Eaton Electrical Group | Yes | Yes |
| Fortin, Marcel | Consultant: Electrical T& D | Yes | Yes |
| Gieger, Jeff | Elastimold/T&B | Yes | Yes |
| Glaesman, Peter | Reuel, Inc | Yes | Yes |
| Hirz, Harry | Joslyn Hi-Voltage | Yes | Yes |
| Jankowich, Edward M. | Thomas & Betts | Yes | Yes |
| LaBianco, Michael | G&W Electric Co |  | Yes |
| Martin, Donald R. | G & W Electric Co |  | Yes |
| Meiners, Steve | General Electric | Yes | Yes |
| Parker, Don | Alabama Pwr / Southern Co. | Yes | Yes |
| Riopel, Sebastien | ECI-ElecroComposites |  | Yes |
| Royster, Timothy E. | Dominion Virginia Power | Yes | Yes |
| Smith, R. Kirkland | Eaton | Yes |  |
| Soulard, Francois | Hydro-Qurebec | Yes | Yes |
| Starcevic, Kresimir | KEMA-Powetest |  | Yes |
| Stavnes, Mark | S&C Electric Co |  | Yes |
| Stone, David T. | DTS Technical Services | Yes | Yes |
| Swank, Jim | Cooper Power Systems | Yes | Yes |
| Tobin, Thomas J. | S & C Electric Company |  | Yes |
| Uzelac, Nenad | G&W | Yes | Yes |
| von Miller, Walt | Consultant | Yes | Yes |
| Walter, Bill | WE Energy |  | Yes |
| Workman, Ken | Schweitzer Engineering Inc |  | Yes |
| Zawadzki, Janusz | Powertech Labs | Yes | Yes |

b) Capacitor Switch Standard C37.66  Working Group Chairman Harry Hirz reported the following:

Standard is now published and available for purchase, date March 2006.

Harry Hirz, requested that a time slot be arranged for next meeting to begin next revision of standard.

c) Underground Switchgear Standard C37.74  Working Group Chairman Steve Meiners reported the following:

The PAR has been approved.

The minutes from the October meeting were reviewed.

NEC 2006 revision to put in service entrance connection rules was rejected due to work by Chuck Ball.   Jerry Baskin will supply documentation. (Attachment 1)

C57 12.30 & 31 is in revision in Transformer group, and the RODE will act as a liaison.

These standards are for enclosure of pole mounted equipment, 30 is pole mounted applications, and 31 is for pole mounted in Coastal Areas.

The minutes from October 2006 were accepted as presented.

Ed Jankowich comments: (Attachment 2)

- Requested that 1247 be referenced in the introduction.  WG didn’t see that this was needed. No action to be taken.

- New entries requested – fused way.  Check against C-37-100 for existing definitions.  Expand 3.4 to include fuses in “protected way” if needed.  Jerry Baskin will follow up

- Paragraph 5 – Ratings, required related capabilities and test requirements.  WG discussed “related test requirements.” (“Related required capability”). Suggestion to remove upper row in Table 1, in 5.2.1.1 and merge in to next row, as appropriate. Steve will draft up a revision for review by the WG

- 6.7.1 to be deleted (the last sentence, referring to errors in older version of 1247).  WG agreed to delete.  Steve will update document text for first Draft.

- 6.7.2.1, first sentence, remove “or greater than”.  Discussion of tolerances, IEC, HV circuit breaker standards. Some of these centers on the capabilities of the labs.  Remove “equal to or greater than the levels” to “as specified.”  Dave Stone will look into IEC standard 62271-1 as a reference.

- 6.7.2.1 – Points of application test voltage, delete V & G from 10 & 11 (redundant with lines 4 & 7).  WG agrees to delete.  Steve will update document text for first Draft.

- 6.7.2.5, paragraph a – Related lightning-impulse withstand voltage test.  Tolerances are covered in Std 4.  Remove tolerance and refer to Std. 4.

- Dave Stone urges the WG to incorporate -100.  Form a task force to examine how to incorporate -100 into -74. (Ray and Dave)

- 6.7.4.1, second & third paragraphs.  Recommend adding reference to 6.7.4.5.  WG feels this to be between the manufacture and lab.  No action required.

- 6.7.5.4 suggest deleting note regarding error in 1247.  WG - Remove.  Steve will update document text for first Draft.

- 6.7.5.6 Same as above. Steve will update document text for first Draft.

- 7.4 does not agree with 6.7.9.1.  No change.

- Section 9 – harmonize with 37-60, section 9.  Ground connections.  Jim Swank will check.

- 9.10, second sentence.  Need Ed to clarify.

- Annex A, Table A.1.  Ask Ed to clarify.

Meeting was adjourned.

Attachment 1

Attachment 2

Attendance – 17 Members & 9 Guest (see Attachment 3)

Note to WG team members!

Action items are in Bold text in the text above.  Please complete this task and return to WG Chair, Steve Meiners, when completed.

Also, team please prepare any other comments in Errata Sheet format for discussion by WG team at our next meeting.

d) Task Force on Controls for Distribution Equipment   Task Force Chairman Don Parker:

Refer to the pdf for the minutes of the meeting.

e) Task Force on Solid Dielectric  Equipment   Task Force Chairman Chris Ambrose & Marcel Fortin chaired this session and reported the following:

Chris Ambrose opened the meeting at 3:45.  The Task Force (TF) members and guests introduced themselves, and the roster was circulated.  A copy of the completed roster is attached separately.  There were 36 people in attendance: 19 members, one corresponding member, and 16 guests.

The minutes of the Fall 2006 meeting were presented and approved.

The new (May 1, 2007) IEEE patent slides were presented. The attendees had no patent issues to report. The full copies of the new patent slides are attached to these minutes.

Chris Ambrose restated the TF theme as laid out in the RODE subcommittee minutes from the October 5, 2005 meeting in Montreal.

# Action items from the last meeting

The main action item was to conduct the literature survey and analysis. Very little progress has been made to this point.

# Overall course of direction

The proposed overall course of action (a conceptual development tool) was presented by the chair as follows:

# Brain storming

Main topics discussed and dealt with were:

- The TF objective and initial direction.

- The past and present RODE Subcommittee chairs reiterated that the initial objective were to:

Develop a set of aging test methods and construction guidelines for switchgear with solid dielectric insulation to be considered by product standards.

- The TF discussed various types of products and potential aging problems.

- The TF discussed membership (see “Membership of Task Force” below).

- Standards (IEC, IEEE, others) that already covers ageing tests on similar materials used in different types of equipments and/or components.

# Membership of Task Force

# It was agreed that membership to the Task Force would be opened to anyone in attendance at this meeting in an effort to generate more interest and enthusiasm for this project.  Several attendees took advantage of this offer and became members of the Task Force.

# Course of action

The following actions items were agreed upon by attendees:

- Every attendees will sent to Marcel Fortin (fortin.marcel@ieee.org) and Chris Ambrose (chris_ambrose@ieee.org) the list of standards (IEEE, IEC, relevant papers, and others) they know that covers some aging tests on solid insulation. Deadline: end of July 2007.

- Chris Ambrose will complete the bibliography search and initiate the bibliography analysis. The attendees who know of some papers that would be useful will send them to Chris Ambrose for end of July 2007.

The meeting was adjourned at 5:00 P.M.

7.   OLD BUSINESS

None.

8.   NEW BUSINESS

  - Need slot for 37.66 (2005) at next meeting (Harry Hirtz).

  - Inquiry to take on another TF faulted circuit indicators, IEEE-495. (Harry Hirz).  Now at ICC.  Will revisit in October.

John Wood was recognized for his leadership of RODE.  John will be retiring form PG&E on June 1.

An interpretation of the C37.74 Switch standard was presented to the sub-committee for consideration.

Review by sub-committee and voted unanimously was to present to the main committee that a switch tested to C37.74 and under Table 7 paragraph 6.7.4.6 must operate three times fault close as a required test for name-plating to this standard.  Any number of operations less than this does not meet the required ratings.

There was reference to standard 1247 and this cannot be commented on by RODE and will be referred to HVS subcommittee.

9. NEXT MEETINGS:

- September 23 – 27, Philadelphia

- Spring 2008, Las Vegas, Portland, Anaheim, Asheville, Nashville

- Fall 2008, Open

Respectively yours,

Steven Meiners

Chairman

RODE Subcommittee

Attachments:

See S07RODEa1 - RODE Standards Status Report.

See S07RODEa2 - RODE Membership Roster