## Sheet1
Repsondent | Market | Use Case/Application | Sub-Application | Throughput | Max Latency | Periodicity | Jitter | Mobility | Upstream/Downstream Ratio | Min # end points/sector* | Max # end points/sector* | What technology is currently used | Bandwidth of existing technology | Comments
Service Provider | Drone | UAS CNPC RADIO LINK |  | 5,000 bps | 60ms | 1 Hz | 20ms | Rapid Movement (vehicular) | 80/20 | 30 | 60 | LTE, 802.16, GMSK, 802.11 | 10KHz - 5MHz
Chevron | Oil/Gas | Pump Off Controller |  | 150,000 bps | N/A | 360 sec | N/A | Fixed | 80/20 | 4 | 400 | MAS | 25KHz Wireless | Enet & Serial Interface
Chevron | Oil/Gas | PtP IP Backhaul | LoRa WAN Gateway | 100,000 bps | <100ms | Cont. | <50ms | Fixed | 80/20 | 1 | 1 | Cellular - 4G
Chevron | Electric | PtP Analog Data Circuit replacement | Transfer Trip/EMS SCADA | 1,000,000 bps | 20ms | Cont. | 5ms | Fixed | 50/50 | 1 | 1 | Lease Line | 3 KHz | Typ. 3ea G7.11 PCM Streams
End User | Electric | Advanced Metering Infrastructure (AMI) |  | 33.8 bps |  |  |  | Fixed
End User | Electric | Volt/VAR Control (Capacitor banks) |  | 240.8 bps | N/A |  |  | Fixed
End User | Electric | Distribution Feeder Automation |  | 722.4 bps |  |  |  | Fixed
End User | Electric | Circuit Sensors |  | 722.4 bps |  |  |  | Fixed
End User | Electric | Advanced Solar Inverters |  | 240.8 bps |  |  |  | Fixed
End User | Electric | Remote Fault Indicators |  | 60.2 bps |  |  |  | Fixed
End User | Water | SCADA |  | 120.4 bps |  |  |  | Fixed
End User | Electric | Substation Monitoring Devices |  | 240.8 bps |  |  |  | Fixed
End User | Electric | Field Devices | Reclosers, Fault Circuit Indicators (FCIs), Switches, Access Points | 9600 bps |  |  |  | Fixed
End User | Electric | AMI Collector |  | 500 bps |  |  |  | Fixed
End User | Electric | Substation |  | 1540000 bps |  |  |  | Fixed
End User | Electric | Distribution Sub SCADA |  | 19,200 bps | < 4sec | Cont. |  | Fixed | 70/30 | 1 | 15 | MAS | 12.5 Khz | Serial
End User | Electric | Distribution Sub Metering |  | 250,000 bps | < 2 sec | 1 day |  | Fixed | 70/30 | 1 | 15 | Spread Spectrum | 1024 Kbps | ethernet
End User | Electric | AMI |  | 250,000 bps | < 2 sec | 30 min |  | Fixed | 70/30 | 1 | 15 | Spread Spectrum | 1024 Kbps | ethernet
* Assume 3 sector site