## Sheet1
Respondent | Market | Use Case/Application | Sub-Application | Throughput | Max Latency | Periodicity | Jitter | Mobility | Upstream / Downstream Ratio | Min # end points/sector* | Max # end points/sector* | Currently Used Technology | Bandwidth of existing technology | Comments
End User | Electric | Distribution Substation SCADA |  | 3300 bps | <100 ms | 4 sec | N/A | Fixed | 30/70 | 2 | 50 | MimoMax | 50 kHz Wireless
End User | Electric | Downline Distribution Automation | Cap bank controller | 1000 bps | N/A | N/A | N/A | Fixed | 30/70 | 12 | 50 | Cellular - 4G
Meteorcomm | Rail | I-ETMS Positive Train Control | Periodic wayside status | 50-350 bps / wayside | < 1 s | 4 s | N/A | Rapid Movement (vehicular) | 10/90 | N/A | N/A | 220 MHz data | 25 kHz Wireless | Between wayside and locomotive
Meteorcomm | Rail | I-ETMS Positive Train Control | Back office to loco | 60-200 bps / locomotive | < 15 s | 1 min | N/A | Rapid Movement (vehicular) | 60/40 | 1 | 50 | 220 MHz data | 25 kHz Wireless | Between base and locomotive
Meteorcomm | Rail | Locomotive Distributed Power |  | 400 bps / locomotive | <100 ms | 2 s | N/A | Rapid Movement (vehicular) | 50/50 | N/A | N/A | 450 MHz data | 12.5 kHz Wireless | Locomotive to locomotive
Meteorcomm | Rail | End-of-Train Communication |  | < 100 bps | <100 ms |  | N/A | Rapid Movement (vehicular) | 90/10 | N/A | N/A | 450 MHz data | 12.5 kHz Wireless | Locomotive to locomotive
Meteorcomm | Rail | Wayside Maintenance |  |  | < 30 s | N/A | N/A | Fixed | 60/40 | 1 | 50 | 220 MHz data, cell data | 25 kHz Wireless | Between base and wayside
Meteorcomm | Rail | Central Traffic Controller Communication |  | < 100 bps / control point | < 1 s | N/A | N/A | Fixed | 70/30 | 1 | 50 | 900 MHz data | 12.5 kHz Wireless | Between base and wayside
Meteorcomm | Rail | Fault detector communication |  | < 50 bps / trackside |  |  | N/A | Fixed | 70/30 |  |  | 45 MHz data, 160 MHz voice | 12.5 kHz Wireless | Trackside to locomotive or base
Meteorcomm | Rail | Grade Crossing Communication | Activation | 250 bps / crossing | < 1 s | N/A | N/A | Rapid Movement (vehicular) | 50/50 | N/A | N/A | 220 MHz data, 160 MHz | 25/12.5 kHz Wireless | Locomotive to trackside
Meteorcomm | Rail | Grade Crossing Communication | Monitoring | < 100 bps / crossing | < 15 s | 4 sec | N/A | Fixed | 90/10 | 1 | 50 | 900 MHz data, 220 Mhz data | 12.5/25 kHz Wireless | Trackside to base
Meteorcomm | Rail | Hy-rail Limits Compliance |  | < 100 bps / Hy-rail | < 1 s | 1 min | N/A | Rapid Movement (vehicular) | 50/50 | 1 | 50 | 45 MHz data, 220 MHz data | 25/12.5 kHz Wireless | Locomotive or Base to Hy-rail
Meteorcomm | Rail | Employee-in-charge |  | < 100 bps | <15 s | N/A | N/A | Slow Movement | 50/50 | N/A | N/A | N/A | N/A | Between work crew and "base"
Meteorcomm | Rail | Worksite protection |  | < 50 bps / crew member | < 1 s | 1 min | N/A | Slow Movement | 70/30 | N/A | N/A | N/A | N/A | Between work crew and "base"
Meteorcomm | Rail | On-board Sensor Network |  | 56 kbps / node | < 1 s | N/A | N/A | Rapid Movement (vehicular) | 50/50 | N/A | N/A | N/A | N/A | Mesh network
Meteorcomm | Rail | Remote Control Locomotive |  | 9600/4800 bps radio | < 100 ms | 2 s | N/A | Slow Movement | 50/50 | N/A | N/A | 450 MHz data, 220 MHz data | 12.5/25 kHz Wireless | Between RCU and locomotive
Meteorcomm | Rail | Drone Communication |  | 9600/4800 bps radio | < 1 s | N/A | N/A | Rapid Movement (vehicular) | 50/50 | N/A | N/A | 900 MHz data | 12.5 kHz Wireless | Between base and drone
Meteorcomm | Rail | Differential GPS |  | 400 bps / reference station | < 1 s | N/A | N/A | Rapid Movement (vehicular) | 10/90 | N/A | N/A | 220 MHz data | 25 kHz Wireless | Reference stations to locomotive
Aura Networks | Drone | UAS Control and Non Payload Communications (CNPC) |  | 5,000 bps | 60ms | 1 Hz | 20ms | Rapid Movement (vehicular) | 80/20 | 30 | 60 | LTE, 802.16, GMSK, 802.11 | 10KHz - 5MHz | UAS velocity is up to the speed of sound
Chevron | Oil/Gas | Pump Off Controller |  | 150,000 bps | N/A | 360 sec | N/A | Fixed | 80/20 | 4 | 400 | MAS | 25KHz Wireless | Enet & Serial Interface
Chevron | Oil/Gas | PtP IP Backhaul | LoRa WAN Gateway | 100,000 bps | <100ms | Cont. | <50ms | Fixed | 80/20 | 1 | 1 | Cellular - 4G
Chevron | Electric | PtP Analog Data Circuit replacement | Transfer Trip/EMS SCADA | 1,000,000 bps | 20ms | Cont. | 5ms | Fixed | 50/50 | 1 | 1 | Lease Line | 3 KHz | Typ. 3ea G7.11 PCM Streams
End User | Electric | Advanced Metering Infrastructure (AMI) |  | 33.8 bps |  |  |  | Fixed
End User | Electric | Volt/VAR Control (Capacitor banks) |  | 240.8 bps | N/A |  |  | Fixed
End User | Electric | Distribution Feeder Automation |  | 722.4 bps |  |  |  | Fixed
End User | Electric | Circuit Sensors |  | 722.4 bps |  |  |  | Fixed
End User | Electric | Advanced Solar Inverters |  | 240.8 bps |  |  |  | Fixed
End User | Electric | Remote Fault Indicators |  | 60.2 bps |  |  |  | Fixed
End User | Water | SCADA |  | 120.4 bps |  |  |  | Fixed
End User | Electric | Substation Monitoring Devices |  | 240.8 bps |  |  |  | Fixed
End User | Electric | Field Devices | Reclosers, Fault Circuit Indicators (FCIs), Switches, Access Points | 9600 bps |  |  |  | Fixed
End User | Electric | AMI Collector |  | 500 bps |  |  |  | Fixed
End User | Electric | Substation |  | 1540000 bps |  |  |  | Fixed
End User | Electric | Distribution Sub SCADA |  | 19,200 bps | < 4sec | Cont. |  | Fixed | 70/30 | 1 | 15 | MAS | 12.5 Khz | Serial
End User | Electric | Distribution Sub Metering |  | 250,000 bps | < 2 sec | 1 day |  | Fixed | 70/30 | 1 | 15 | Spread Spectrum | 1024 Kbps | ethernet
End User | Electric | AMI |  | 250,000 bps | < 2 sec | 30 min |  | Fixed | 70/30 | 1 | 15 | Spread Spectrum | 1024 Kbps | ethernet
Heuristic Actions | Rail/DOT | Bridge & Infrastructure Monitoring |  | 10-500 kbps |  | 1-20 polls per day |  | Fixed | 80/20 | 5 | 60 | LTE
* Assume 3 sector site